## Survey Data
Station | Northing (m) | Easting (m) | Elevation (m) | Description
0+000.00 | 9869157.075 | 787472.264 | 1873.175 | Borehole
0+020.00 | 9869146.9267 | 787455.0355 | 1873.21 | Spotheight
0+040.00 | 9869135.8551 | 787438.381 | 1873.249 | Spotheight
0+060.00 | 9869124.9273 | 787421.6333 | 1873.356 | Spotheight
0+080.00 | 9869116.1636 | 787403.6666 | 1873.508 | Spotheight
0+100.00 | 9869106.5639 | 787386.1215 | 1873.635 | Spotheight
0+120.00 | 9869096.6369 | 787368.7632 | 1873.688 | Spotheight
0+140.00 | 9869086.3108 | 787351.6381 | 1873.754 | Spotheight
0+160.00 | 9869075.4645 | 787334.8542 | 1873.816 | Spotheight
0+180.00 | 9869064.9601 | 787317.8543 | 1873.865 | Spotheight
0+200.00 | 9869057.8535 | 787299.1809 | 1873.957 | Spotheight
0+220.00 | 9869051.6882 | 787280.1778 | 1873.98 | Spotheight
0+240.00 | 9869044.51 | 787261.5172 | 1873.995 | Spotheight
0+260.00 | 9869036.1064 | 787243.3976 | 1873.996 | Nkairowuani Kiosk 1
0+280.00 | 9869024.2022 | 787227.628 | 1873.997 | Spotheight
0+300.00 | 9869005.5321 | 787220.5775 | 1873.873 | Spotheight
0+320.00 | 9868986.0567 | 787216.0361 | 1873.725 | Spotheight
0+340.00 | 9868966.5553 | 787211.5982 | 1873.568 | Spotheight
0+360.00 | 9868946.9542 | 787207.6792 | 1873.397 | Spotheight
0+380.00 | 9868927.1914 | 787204.6078 | 1873.205 | Spotheight
0+400.00 | 9868907.747 | 787200.0786 | 1873.02 | Spotheight
0+420.00 | 9868888.5179 | 787194.5794 | 1872.841 | Spotheight
0+440.00 | 9868871.4438 | 787184.3609 | 1872.705 | Spotheight
0+460.00 | 9868854.5996 | 787173.6492 | 1872.573 | Spotheight
0+480.00 | 9868835.7443 | 787166.98 | 1872.385 | Spotheight
0+500.00 | 9868816.5621 | 787161.5966 | 1872.226 | Spotheight
0+520.00 | 9868796.775 | 787158.6866 | 1872.067 | Spotheight
0+540.00 | 9868777.8583 | 787153.1486 | 1871.927 | Spotheight
0+560.00 | 9868760.7253 | 787142.8305 | 1871.792 | Spotheight
0+580.00 | 9868742.7192 | 787134.2579 | 1871.663 | Spotheight
0+600.00 | 9868724.154 | 787126.8192 | 1871.516 | Spotheight
0+620.00 | 9868704.7627 | 787122.2944 | 1870.674 | Nkairowuani lagga
0+640.00 | 9868685.0949 | 787118.7909 | 1871.618 | Spotheight
0+660.00 | 9868665.1272 | 787117.6557 | 1871.598 | Spotheight
0+680.00 | 9868645.6318 | 787113.6606 | 1871.616 | Spotheight
0+700.00 | 9868626.4037 | 787108.1577 | 1871.653 | Spotheight
0+720.00 | 9868607.6465 | 787101.2543 | 1871.7 | Spotheight
0+740.00 | 9868588.9344 | 787094.2155 | 1871.749 | Spotheight
0+760.00 | 9868569.7319 | 787088.6242 | 1871.806 | Spotheight
0+780.00 | 9868550.7382 | 787082.4482 | 1871.907 | Spotheight
0+800.00 | 9868532.3948 | 787074.4783 | 1872.147 | Spotheight
0+820.00 | 9868513.5359 | 787068.0393 | 1872.325 | Spotheight
0+840.00 | 9868494.0731 | 787063.4348 | 1872.442 | Spotheight
0+860.00 | 9868474.3044 | 787060.6217 | 1872.6 | Spotheight
0+880.00 | 9868454.4113 | 787058.5565 | 1872.818 | Spotheight
0+900.00 | 9868434.5045 | 787056.6287 | 1872.957 | Spotheight
0+920.00 | 9868414.6117 | 787054.5917 | 1873.117 | Spotheight
0+940.00 | 9868394.8647 | 787051.421 | 1873.392 | Spotheight
0+960.00 | 9868375.0727 | 787048.6679 | 1873.659 | Spotheight
0+980.00 | 9868355.0957 | 787047.7095 | 1873.884 | Spotheight
1+000.00 | 9868335.1365 | 787046.5014 | 1874.113 | Spotheight
1+020.00 | 9868315.2273 | 787044.5972 | 1874.354 | Spotheight
1+040.00 | 9868295.3182 | 787042.6929 | 1874.552 | Spotheight
1+060.00 | 9868275.409 | 787040.7887 | 1874.701 | Spotheight
1+080.00 | 9868255.4999 | 787038.8844 | 1874.908 | Spotheight
1+100.00 | 9868235.588 | 787037.0148 | 1875.164 | Spotheight
1+120.00 | 9868215.6241 | 787035.8139 | 1875.371 | Spotheight
1+140.00 | 9868195.6615 | 787034.5953 | 1875.588 | Spotheight
1+160.00 | 9868175.7504 | 787032.7115 | 1875.835 | Spotheight
1+180.00 | 9868155.8536 | 787030.6967 | 1876.093 | Spotheight
1+200.00 | 9868136.005 | 787028.2409 | 1876.398 | Spotheight
1+220.00 | 9868116.0961 | 787026.3752 | 1876.613 | Spotheight
1+240.00 | 9868096.1599 | 787024.7785 | 1876.833 | Spotheight
1+260.00 | 9868076.2917 | 787022.5113 | 1877.068 | Spotheight
1+280.00 | 9868056.4411 | 787020.0717 | 1877.328 | Spotheight
1+300.00 | 9868036.5354 | 787018.1438 | 1877.547 | Spotheight
1+320.00 | 9868016.6189 | 787016.3189 | 1877.752 | Spotheight
1+340.00 | 9867996.6963 | 787014.5604 | 1877.925 | Spotheight
1+360.00 | 9867976.7717 | 787012.8259 | 1878.105 | Spotheight
1+380.00 | 9867956.8441 | 787011.1255 | 1878.325 | Spotheight
1+400.00 | 9867937.0649 | 787013.5657 | 1878.432 | Spotheight
1+420.00 | 9867917.5156 | 787017.6274 | 1878.519 | Spotheight
1+440.00 | 9867898.3739 | 787023.4233 | 1878.589 | Spotheight
1+460.00 | 9867879.5287 | 787030.0937 | 1878.669 | Spotheight
1+480.00 | 9867860.8159 | 787037.1527 | 1878.753 | Spotheight
1+500.00 | 9867841.5833 | 787042.5974 | 1878.876 | Spotheight
1+520.00 | 9867822.2674 | 787047.7819 | 1879.003 | Spotheight
1+540.00 | 9867803.1678 | 787053.7152 | 1879.077 | Spotheight
1+560.00 | 9867783.9946 | 787059.3291 | 1879.153 | Spotheight
1+580.00 | 9867764.0049 | 787058.7762 | 1879.261 | Spotheight
1+600.00 | 9867744.0207 | 787058.034 | 1879.376 | Spotheight
1+620.00 | 9867724.0762 | 787056.5446 | 1879.523 | Spotheight
1+640.00 | 9867704.2055 | 787054.4662 | 1879.674 | Spotheight
1+660.00 | 9867684.5246 | 787050.9079 | 1879.834 | Spotheight
1+680.00 | 9867664.7584 | 787047.9879 | 1879.991 | Spotheight
1+700.00 | 9867644.829 | 787046.308 | 1880.144 | Spotheight
1+720.00 | 9867624.9451 | 787044.2252 | 1880.287 | Spotheight
1+740.00 | 9867605.1445 | 787041.4079 | 1880.412 | Spotheight
1+760.00 | 9867585.331 | 787038.6945 | 1880.538 | Spotheight
1+780.00 | 9867565.4451 | 787036.561 | 1880.673 | Spotheight
1+800.00 | 9867545.5451 | 787034.6018 | 1880.804 | Spotheight
1+820.00 | 9867525.5723 | 787033.5608 | 1880.92 | Spotheight
1+840.00 | 9867505.6358 | 787032.2253 | 1881.038 | Spotheight
1+860.00 | 9867486.2931 | 787027.1401 | 1881.192 | Spotheight
1+880.00 | 9867467.0189 | 787021.8222 | 1881.345 | Spotheight
1+900.00 | 9867448.0196 | 787015.575 | 1881.495 | Spotheight
1+920.00 | 9867429.3258 | 787008.599 | 1881.641 | Spotheight
1+940.00 | 9867411.6804 | 786999.1843 | 1881.777 | Spotheight
1+960.00 | 9867393.8738 | 786990.0996 | 1881.923 | Spotheight
1+980.00 | 9867375.5743 | 786982.0295 | 1882.1 | Spotheight
2+000.00 | 9867357.1674 | 786974.2147 | 1882.264 | Spotheight
2+020.00 | 9867338.5957 | 786966.7923 | 1882.407 | Spotheight
2+040.00 | 9867320.2293 | 786958.9283 | 1882.556 | Spotheight
2+060.00 | 9867302.6497 | 786949.3911 | 1882.724 | Spotheight
2+080.00 | 9867284.8706 | 786940.2927 | 1882.894 | Spotheight
2+100.00 | 9867266.0061 | 786933.6494 | 1883.071 | Spotheight
2+120.00 | 9867247.0958 | 786927.139 | 1883.232 | Spotheight
2+140.00 | 9867228.1538 | 786920.7202 | 1883.382 | Spotheight
2+160.00 | 9867210.3269 | 786911.7944 | 1883.589 | Spotheight
2+180.00 | 9867192.9048 | 786901.9742 | 1883.813 | Spotheight
2+200.00 | 9867175.0435 | 786892.9758 | 1883.966 | Spotheight
2+220.00 | 9867157.1182 | 786884.1093 | 1884.124 | Spotheight
2+240.00 | 9867138.981 | 786875.6807 | 1884.294 | Spotheight
2+260.00 | 9867121.5562 | 786865.933 | 1884.492 | Spotheight
2+280.00 | 9867104.5898 | 786855.3433 | 1884.708 | Spotheight
2+300.00 | 9867086.7464 | 786846.3118 | 1884.816 | Spotheight
2+320.00 | 9867068.8452 | 786837.3954 | 1884.928 | Spotheight
2+340.00 | 9867050.6954 | 786828.9941 | 1885.077 | Spotheight
2+360.00 | 9867032.5523 | 786820.578 | 1885.246 | Spotheight
2+380.00 | 9867014.4265 | 786812.1251 | 1885.464 | Spotheight
2+400.00 | 9866996.3523 | 786803.5634 | 1885.657 | Spotheight
2+420.00 | 9866978.3618 | 786794.8262 | 1885.81 | Spotheight
2+440.00 | 9866961.0668 | 786784.8318 | 1885.976 | Spotheight
2+460.00 | 9866944.1288 | 786774.1967 | 1886.15 | Spotheight
2+480.00 | 9866927.2381 | 786763.487 | 1886.318 | Spotheight
2+500.00 | 9866910.3713 | 786752.7394 | 1886.482 | Spotheight
2+520.00 | 9866893.9381 | 786741.3445 | 1886.605 | Spotheight
2+540.00 | 9866877.5851 | 786729.8302 | 1886.721 | Spotheight
2+560.00 | 9866862.0463 | 786717.2523 | 1886.882 | Spotheight
2+580.00 | 9866846.6737 | 786704.4584 | 1887.053 | Spotheight
2+600.00 | 9866831.0631 | 786691.9571 | 1887.218 | Spotheight
2+620.00 | 9866815.4096 | 786679.5084 | 1887.383 | Spotheight
2+640.00 | 9866800.1112 | 786666.6274 | 1887.578 | Spotheight
2+660.00 | 9866784.7818 | 786653.7897 | 1887.774 | Spotheight
2+680.00 | 9866767.4951 | 786643.7317 | 1887.916 | Spotheight
2+700.00 | 9866750.2544 | 786633.5956 | 1888.044 | Spotheight
2+720.00 | 9866732.4822 | 786633.2271 | 1888.138 | Spotheight
2+740.00 | 9866718.9436 | 786647.948 | 1888.222 | Spotheight
2+760.00 | 9866706.768 | 786663.8052 | 1888.211 | Spotheight
2+780.00 | 9866694.739 | 786679.7834 | 1888.187 | Spotheight
2+800.00 | 9866682.3763 | 786695.5046 | 1888.156 | Spotheight
2+820.00 | 9866669.9996 | 786711.215 | 1888.125 | Spotheight
2+840.00 | 9866657.5873 | 786726.8973 | 1888.089 | Spotheight
2+860.00 | 9866645.157 | 786742.5653 | 1888.051 | Spotheight
2+880.00 | 9866632.7263 | 786758.2331 | 1888.011 | Spotheight
2+900.00 | 9866620.2937 | 786773.8993 | 1887.959 | Spotheight
2+920.00 | 9866607.8611 | 786789.5655 | 1887.907 | Spotheight
2+940.00 | 9866595.4638 | 786805.2597 | 1887.859 | Spotheight
2+960.00 | 9866583.0719 | 786820.9581 | 1887.811 | Spotheight
2+980.00 | 9866570.7853 | 786836.7387 | 1887.763 | Spotheight
3+000.00 | 9866558.5673 | 786852.5729 | 1887.716 | Spotheight
3+020.00 | 9866546.3317 | 786868.3934 | 1887.672 | Spotheight
3+040.00 | 9866534.0891 | 786884.2086 | 1887.631 | Spotheight
3+060.00 | 9866521.8199 | 786900.003 | 1887.589 | Spotheight
3+080.00 | 9866509.511 | 786915.7667 | 1887.547 | Spotheight
3+100.00 | 9866497.2059 | 786931.5332 | 1887.494 | Spotheight
3+120.00 | 9866484.9063 | 786947.3041 | 1887.421 | Spotheight
3+140.00 | 9866472.5721 | 786963.0478 | 1887.354 | Spotheight
3+160.00 | 9866460.2062 | 786978.7668 | 1887.29 | Spotheight
3+180.00 | 9866447.7293 | 786994.3974 | 1887.196 | Spotheight
3+200.00 | 9866435.2081 | 787009.9929 | 1887.091 | Spotheight
3+220.00 | 9866422.7976 | 787025.676 | 1886.984 | Spotheight
3+240.00 | 9866410.5022 | 787041.4502 | 1886.875 | Spotheight
3+260.00 | 9866398.0637 | 787057.1107 | 1886.765 | Spotheight
3+280.00 | 9866385.4896 | 787072.6635 | 1886.653 | Spotheight
3+300.00 | 9866373.1246 | 787088.3819 | 1886.519 | Spotheight
3+320.00 | 9866360.8792 | 787104.1949 | 1886.373 | Spotheight
3+340.00 | 9866348.5533 | 787119.9451 | 1886.237 | Spotheight
3+360.00 | 9866336.2101 | 787135.6819 | 1886.103 | Spotheight
3+380.00 | 9866323.8036 | 787151.3687 | 1885.965 | Spotheight
3+400.00 | 9866311.3814 | 787167.0432 | 1885.825 | Spotheight
3+420.00 | 9866299.0309 | 787182.774 | 1885.692 | Spotheight
3+440.00 | 9866286.7418 | 787198.553 | 1885.565 | Spotheight
3+460.00 | 9866274.2937 | 787214.2044 | 1885.431 | Spotheight
3+480.00 | 9866261.5326 | 787229.6041 | 1885.285 | Spotheight
3+500.00 | 9866247.8599 | 787244.1296 | 1885.156 | Spotheight
3+520.00 | 9866232.9471 | 787257.4566 | 1885.049 | Spotheight
3+540.00 | 9866215.957 | 787267.8011 | 1884.949 | Spotheight
3+560.00 | 9866198.2204 | 787277.043 | 1884.853 | Spotheight
3+580.00 | 9866179.9396 | 787285.1354 | 1884.775 | Spotheight
3+600.00 | 9866161.545 | 787292.9866 | 1884.701 | Spotheight
3+620.00 | 9866143.2519 | 787301.0708 | 1884.599 | Spotheight
3+640.00 | 9866124.9637 | 787309.1663 | 1884.494 | Spotheight
3+660.00 | 9866106.5345 | 787316.9356 | 1884.413 | Spotheight
3+680.00 | 9866088.2155 | 787324.9545 | 1884.329 | Spotheight
3+700.00 | 9866070.0665 | 787333.3576 | 1884.241 | Spotheight
3+720.00 | 9866051.8717 | 787341.6608 | 1884.162 | Spotheight
3+740.00 | 9866033.6517 | 787349.909 | 1884.055 | Spotheight
3+760.00 | 9866015.2999 | 787357.857 | 1883.987 | Spotheight
3+780.00 | 9865996.8987 | 787365.6924 | 1883.932 | Spotheight
3+800.00 | 9865978.4507 | 787373.4172 | 1883.838 | Spotheight
3+820.00 | 9865960.0007 | 787381.137 | 1883.741 | Spotheight
3+840.00 | 9865941.5758 | 787388.9166 | 1883.645 | Spotheight
3+860.00 | 9865923.1619 | 787396.7223 | 1883.549 | Spotheight
3+880.00 | 9865904.8333 | 787404.7242 | 1883.461 | Spotheight
3+900.00 | 9865886.565 | 787412.8648 | 1883.379 | Spotheight
3+920.00 | 9865868.6928 | 787421.767 | 1883.299 | Spotheight
3+940.00 | 9865851.5768 | 787432.1131 | 1883.224 | Spotheight
3+960.00 | 9865836.41 | 787444.8937 | 1883.123 | Spotheight
3+980.00 | 9865822.7297 | 787459.4832 | 1883.004 | Spotheight
4+000.00 | 9865808.5105 | 787473.54 | 1882.902 | Spotheight
4+020.00 | 9865794.0812 | 787487.389 | 1882.808 | Spotheight
4+040.00 | 9865779.5745 | 787501.1568 | 1882.695 | Spotheight
4+060.00 | 9865765.101 | 787514.9562 | 1882.578 | Spotheight
4+080.00 | 9865751.7685 | 787529.864 | 1882.463 | Spotheight
4+100.00 | 9865738.1967 | 787544.5385 | 1882.349 | Spotheight
4+120.00 | 9865723.5751 | 787558.1843 | 1882.237 | Spotheight
4+140.00 | 9865709.146 | 787572.0292 | 1882.122 | Spotheight
4+160.00 | 9865695.0236 | 787586.1911 | 1882.002 | Spotheight
4+180.00 | 9865680.9283 | 787600.3799 | 1881.894 | Spotheight
4+200.00 | 9865666.8615 | 787614.5969 | 1881.798 | Spotheight
4+220.00 | 9865652.5787 | 787628.5939 | 1881.681 | Spotheight
4+240.00 | 9865638.099 | 787642.3902 | 1881.546 | Spotheight
4+260.00 | 9865623.8519 | 787656.4238 | 1881.429 | Spotheight
4+280.00 | 9865609.7725 | 787670.6284 | 1881.323 | Spotheight
4+300.00 | 9865595.6099 | 787684.7485 | 1881.217 | Spotheight
4+320.00 | 9865581.1949 | 787698.6124 | 1881.108 | Spotheight
4+340.00 | 9865566.829 | 787712.5267 | 1880.998 | Spotheight
4+360.00 | 9865552.6077 | 787726.5892 | 1880.885 | Spotheight
4+380.00 | 9865538.3864 | 787740.6518 | 1880.778 | Spotheight
4+400.00 | 9865524.1652 | 787754.7143 | 1880.68 | Spotheight
4+420.00 | 9865509.7958 | 787768.6239 | 1880.592 | Spotheight
4+440.00 | 9865495.2795 | 787782.3817 | 1880.516 | Spotheight
4+460.00 | 9865480.9259 | 787796.3085 | 1880.448 | Spotheight
4+480.00 | 9865466.6257 | 787810.2907 | 1880.381 | Spotheight
4+500.00 | 9865452.2389 | 787824.1839 | 1880.32 | Spotheight
4+520.00 | 9865437.8323 | 787838.0565 | 1880.26 | Spotheight
4+540.00 | 9865423.3475 | 787851.8471 | 1880.221 | Spotheight
4+560.00 | 9865408.8115 | 787865.5841 | 1880.196 | Spotheight
4+580.00 | 9865394.405 | 787879.4545 | 1880.159 | Spotheight
4+600.00 | 9865380.2453 | 787893.579 | 1880.102 | Spotheight
4+620.00 | 9865365.8463 | 787907.4563 | 1880.067 | Spotheight
4+640.00 | 9865351.2658 | 787921.146 | 1880.049 | Spotheight
4+660.00 | 9865336.9408 | 787935.1021 | 1880.006 | Spotheight
4+680.00 | 9865322.6598 | 787949.104 | 1879.96 | Spotheight
4+700.00 | 9865307.8236 | 787962.5158 | 1879.925 | Spotheight
4+720.00 | 9865292.9776 | 787975.9171 | 1879.889 | Spotheight
4+740.00 | 9865278.5997 | 787989.8193 | 1879.9 | Spotheight
4+760.00 | 9865264.2386 | 788003.7387 | 1879.902 | Spotheight
4+780.00 | 9865250.1537 | 788017.9379 | 1879.692 | Spotheight
4+800.00 | 9865236.0689 | 788032.1371 | 1879.482 | Spotheight
4+820.00 | 9865222.018 | 788046.3699 | 1879.322 | Spotheight
4+832.87 | 9865212.989 | 788055.536 | 1879.234 | Nkairowuani Kiosk 2

## Water Demand
Item | Units
B.H Yield | 8.5 | m³/Hr
Population Targeted | 2000 | people
Water demand per capita | 20 | L/d/p
Total Water Demand per day | 40000 | Litres
Reservoir capacity required (tank) | 40 | m³
Reservoir | 100 | m³
Unmet Demand | -60 | m³
Note:
20 litres per capita per day should be assured to take care of basic hygiene needs and basic food hygiene (WHO)
Assumption: | 1 day | 8 hrs | Pump operational for10 hrs

## Pump Design
BOREHOLE DATA
BH depth (m) = | 200 | Max Disccharge | Pump Operational Factor of Safety
Pump Water level (m) = | 149.75
Yield (m3/hr) = | 8.5 | 5.6667 | 66.67%
HEAD CALCULATIIONS
Pump level |  |  | 149.75
Frictional Losses |  |  | 19.8746
delivery head |  |  | 50
Tank height |  |  | 1.5
Residual head | 15% |  | 10.7062
Total Head |  |  | 231.8307
POWER REQUIREMENT
H (m) | Q (L/Sec) | Constant | Pump efficiency |  | KW
231.8307 | 1.5741 | 102 | 0.65 |  | 5.5041
Add factor safety |  |  | 1.5 | 8.2561 | KW
|  |  |  | 10.3201 | KVA
PUMP RECOMMENDATIONS
Dayliff DS 8/50 | Power | 7.5 Kw
| Discharge | m3/hr | Head | m
| Min Q | 5 | Hmax | 240
| Max Q | 11 | Hmin | 130
Insert Alternative B | Power
| Discharge | m3/hr | Head | m
| Min Q |  | Hmax
| Max Q |  | Hmin
Insert Alternative C | Power
| Discharge | m3/hr | Head | m
| Min Q |  | Hmax
| Max Q |  | Hmin

## Rising Main - Tank & WK2
ILMOCHIN WATER PROJECT
Contract No.: | [17 empty] | Soil Cover | 1 |  | Assumption: | Discharge | 0.0015741
Profile levels - end of line included
Date:20.09.2022 | [27 empty] | Pipe Details
Nodes | Station | Northing(m) | Easting(m) | Elevation(m) | Chainage | Length (m) | Orig. Ground Level | Discharge (m3/s) | Internal diameter (m) | Area (m2) | Velocity (m/s) | C | HL | Vf | El Static | EL | HGL | Slope (%) | Pipe invert (m) | Depth of excavation (m) | Hp | Hs | Off-take (m3/s) | Total flow (m3/s) | Bends | Losses due to bends | Remarks | External Diameter (mm) | Internal Diameter (mm) | Wall Thickness (mm) | Class | Soil Type
| 0+000.00 | 9855724.132 | 778735.343 | 1835.83 | 0 | 0 | 1835.83 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0 | 0.021756 | 1916.9107 | 1916.9107 | 1916.889 |  | 1834.83 | 1 | 82.059 | 82.0807 |  | 0.0015741 |  |  | Top Borehole Casing Cover START | 63 | 55.4 | 3.8 | PN 10.0
| 0+020.00 | 9855710.4024 | 778749.8859 | 1835.523 | 20 | 20 | 1835.523 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1916.7409 | 1916.7191 | -1.535% | 1834.523 | 1 | 82.1961 | 82.3877 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+040.00 | 9855696.6727 | 778764.4289 | 1835.652 | 40 | 20 | 1835.652 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1916.571 | 1916.5492 | 0.645% | 1834.652 | 1 | 81.8972 | 82.2587 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+060.00 | 9855682.9431 | 778778.9718 | 1835.798 | 60 | 20 | 1835.798 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1916.4011 | 1916.3794 | 0.73% | 1834.798 | 1 | 81.5814 | 82.1127 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+080.00 | 9855681.8701 | 778794.6636 | 1835.987 | 80 | 20 | 1835.987 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1916.2313 | 1916.2095 | 0.945% | 1834.987 | 1 | 81.2225 | 81.9237 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+100.00 | 9855696.7829 | 778807.9906 | 1836.217 | 100 | 20 | 1836.217 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1916.0614 | 1916.0396 | 1.15% | 1835.217 | 1 | 80.8226 | 81.6937 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+120.00 | 9855711.6957 | 778821.3176 | 1836.333 | 120 | 20 | 1836.333 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1915.8915 | 1915.8698 | 0.58% | 1835.333 | 1 | 80.5368 | 81.5777 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+140.00 | 9855726.6084 | 778834.6446 | 1836.487 | 140 | 20 | 1836.487 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1915.7217 | 1915.6999 | 0.77% | 1835.487 | 1 | 80.2129 | 81.4237 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+160.00 | 9855741.5212 | 778847.9716 | 1836.646 | 160 | 20 | 1836.646 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1915.5518 | 1915.53 | 0.795% | 1835.646 | 1 | 79.884 | 81.2647 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+180.00 | 9855756.434 | 778861.2986 | 1836.832 | 180 | 20 | 1836.832 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1915.3819 | 1915.3602 | 0.93% | 1835.832 | 1 | 79.5282 | 81.0787 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+200.00 | 9855771.3468 | 778874.6256 | 1836.999 | 200 | 20 | 1836.999 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1915.2121 | 1915.1903 | 0.835% | 1835.999 | 1 | 79.1913 | 80.9117 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+220.00 | 9855786.2596 | 778887.9526 | 1837.109 | 220 | 20 | 1837.109 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1915.0422 | 1915.0204 | 0.55% | 1836.109 | 1 | 78.9114 | 80.8017 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+240.00 | 9855801.1724 | 778901.2796 | 1837.26 | 240 | 20 | 1837.26 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1914.8723 | 1914.8506 | 0.755% | 1836.26 | 1 | 78.5906 | 80.6507 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+260.00 | 9855816.0851 | 778914.6066 | 1837.37 | 260 | 20 | 1837.37 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1914.7025 | 1914.6807 | 0.55% | 1836.37 | 1 | 78.3107 | 80.5407 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+280.00 | 9855830.9979 | 778927.9336 | 1837.471 | 280 | 20 | 1837.471 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1914.5326 | 1914.5108 | 0.505% | 1836.471 | 1 | 78.0398 | 80.4397 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+300.00 | 9855845.9107 | 778941.2606 | 1837.574 | 300 | 20 | 1837.574 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1914.3627 | 1914.341 | 0.515% | 1836.574 | 1 | 77.767 | 80.3367 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+320.00 | 9855860.8235 | 778954.5876 | 1837.696 | 320 | 20 | 1837.696 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1914.1928 | 1914.1711 | 0.61% | 1836.696 | 1 | 77.4751 | 80.2147 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+340.00 | 9855873.4098 | 778969.4481 | 1837.792 | 340 | 20 | 1837.792 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1914.023 | 1914.0012 | 0.48% | 1836.792 | 1 | 77.2092 | 80.1187 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+360.00 | 9855862.8176 | 778985.7916 | 1838.031 | 360 | 20 | 1838.031 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1913.8531 | 1913.8314 | 1.195% | 1837.031 | 1 | 76.8004 | 79.8797 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+380.00 | 9855849.7276 | 779000.9127 | 1838.242 | 380 | 20 | 1838.242 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1913.6832 | 1913.6615 | 1.055% | 1837.242 | 1 | 76.4195 | 79.6687 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+400.00 | 9855836.6375 | 779016.0339 | 1838.489 | 400 | 20 | 1838.489 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1913.5134 | 1913.4916 | 1.235% | 1837.489 | 1 | 76.0026 | 79.4217 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+420.00 | 9855823.5474 | 779031.1551 | 1838.718 | 420 | 20 | 1838.718 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1913.3435 | 1913.3218 | 1.145% | 1837.718 | 1 | 75.6038 | 79.1927 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+440.00 | 9855810.4573 | 779046.2763 | 1838.986 | 440 | 20 | 1838.986 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1913.1736 | 1913.1519 | 1.34% | 1837.986 | 1 | 75.1659 | 78.9247 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+460.00 | 9855797.3325 | 779061.3659 | 1839.228 | 460 | 20 | 1839.228 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1913.0038 | 1912.982 | 1.21% | 1838.228 | 1 | 74.754 | 78.6827 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+480.00 | 9855779.6723 | 779070.4552 | 1839.411 | 480 | 20 | 1839.411 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1912.8339 | 1912.8121 | 0.915% | 1838.411 | 1 | 74.4011 | 78.4997 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+500.00 | 9855761.2525 | 779078.2467 | 1839.535 | 500 | 20 | 1839.535 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1912.664 | 1912.6423 | 0.62% | 1838.535 | 1 | 74.1073 | 78.3757 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+520.00 | 9855742.8326 | 779086.0383 | 1839.608 | 520 | 20 | 1839.608 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1912.4942 | 1912.4724 | 0.365% | 1838.608 | 1 | 73.8644 | 78.3027 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+540.00 | 9855724.4127 | 779093.8298 | 1839.69 | 540 | 20 | 1839.69 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1912.3243 | 1912.3025 | 0.41% | 1838.69 | 1 | 73.6125 | 78.2207 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+560.00 | 9855705.9928 | 779101.6213 | 1839.719 | 560 | 20 | 1839.719 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1912.1544 | 1912.1327 | 0.145% | 1838.719 | 1 | 73.4137 | 78.1917 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+580.00 | 9855687.5729 | 779109.4129 | 1839.792 | 580 | 20 | 1839.792 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1911.9846 | 1911.9628 | 0.365% | 1838.792 | 1 | 73.1708 | 78.1187 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+600.00 | 9855669.1531 | 779117.2044 | 1839.795 | 600 | 20 | 1839.795 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1911.8147 | 1911.7929 | 0.38% | 1838.795 | 1 | 72.9979 | 78.1157 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+620.00 | 9855650.7332 | 779124.996 | 1839.84 | 620 | 20 | 1839.84 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1911.6448 | 1911.6231 | 0.24% | 1838.84 | 1 | 72.7831 | 78.0707 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+640.00 | 9855632.3133 | 779132.7875 | 1839.894 | 640 | 20 | 1839.894 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1911.475 | 1911.4532 | 0.495% | 1838.894 | 1 | 72.5592 | 78.0167 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+660.00 | 9855613.8934 | 779140.579 | 1839.913 | 660 | 20 | 1839.913 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1911.3051 | 1911.2833 | 0.365% | 1838.913 | 1 | 72.3703 | 77.9977 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+680.00 | 9855595.4798 | 779148.3852 | 1839.944 | 680 | 20 | 1839.944 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1911.1352 | 1911.1135 | 0.25% | 1838.944 | 1 | 72.1695 | 77.9667 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+700.00 | 9855577.093 | 779156.2546 | 1840 | 700 | 20 | 1840 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1910.9654 | 1910.9436 | 0.435% | 1839 | 1 | 71.9436 | 77.9107 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+720.00 | 9855558.7063 | 779164.124 | 1840.022 | 720 | 20 | 1840.022 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1910.7955 | 1910.7737 | 0.39% | 1839.022 | 1 | 71.7517 | 77.8887 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+740.00 | 9855540.3195 | 779171.9934 | 1840.019 | 740 | 20 | 1840.019 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1910.6256 | 1910.6039 | 0.095% | 1839.019 | 1 | 71.5849 | 77.8917 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+760.00 | 9855521.9328 | 779179.8628 | 1840.021 | 760 | 20 | 1840.021 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1910.4558 | 1910.434 | -0.005% | 1839.021 | 1 | 71.413 | 77.8897 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+780.00 | 9855503.546 | 779187.7322 | 1840.031 | 780 | 20 | 1840.031 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1910.2859 | 1910.2641 | 0.06% | 1839.031 | 1 | 71.2331 | 77.8797 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+800.00 | 9855485.1593 | 779195.6016 | 1840.05 | 800 | 20 | 1840.05 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1910.116 | 1910.0943 | 0.145% | 1839.05 | 1 | 71.0443 | 77.8607 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+820.00 | 9855466.7725 | 779203.471 | 1840.077 | 820 | 20 | 1840.077 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1909.9461 | 1909.9244 | 0.23% | 1839.077 | 1 | 70.8474 | 77.8337 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+840.00 | 9855448.3858 | 779211.3404 | 1840.094 | 840 | 20 | 1840.094 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1909.7763 | 1909.7545 | 0.22% | 1839.094 | 1 | 70.6605 | 77.8167 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+860.00 | 9855429.999 | 779219.2098 | 1840.037 | 860 | 20 | 1840.037 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1909.6064 | 1909.5847 | -0.2% | 1839.037 | 1 | 70.5477 | 77.8737 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+880.00 | 9855411.6123 | 779227.0792 | 1840.041 | 880 | 20 | 1840.041 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1909.4365 | 1909.4148 | -0.265% | 1839.041 | 1 | 70.3738 | 77.8697 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+900.00 | 9855393.2255 | 779234.9486 | 1840.062 | 900 | 20 | 1840.062 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1909.2667 | 1909.2449 | 0.125% | 1839.062 | 1 | 70.1829 | 77.8487 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+920.00 | 9855374.8388 | 779242.818 | 1840.056 | 920 | 20 | 1840.056 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1909.0968 | 1909.0751 | 0.075% | 1839.056 | 1 | 70.0191 | 77.8547 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+940.00 | 9855356.452 | 779250.6874 | 1840.025 | 940 | 20 | 1840.025 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1908.9269 | 1908.9052 | -0.185% | 1839.025 | 1 | 69.8802 | 77.8857 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+960.00 | 9855338.0653 | 779258.5568 | 1840.046 | 960 | 20 | 1840.046 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1908.7571 | 1908.7353 | -0.05% | 1839.046 | 1 | 69.6893 | 77.8647 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+980.00 | 9855319.6785 | 779266.4261 | 1840.066 | 980 | 20 | 1840.066 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1908.5872 | 1908.5654 | 0.205% | 1839.066 | 1 | 69.4994 | 77.8447 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+000.00 | 9855301.2918 | 779274.2955 | 1840.068 | 1000 | 20 | 1840.068 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1908.4173 | 1908.3956 | 0.11% | 1839.068 | 1 | 69.3276 | 77.8427 |  |  |  |  | Double Orifice ARV DN63 PN10 | 63 | 55.4 | 3.8 | PN 10.0
| 1+020.00 | 9855282.905 | 779282.1649 | 1840.062 | 1020 | 20 | 1840.062 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1908.2475 | 1908.2257 | -0.02% | 1839.062 | 1 | 69.1637 | 77.8487 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+040.00 | 9855264.5183 | 779290.0343 | 1840.054 | 1040 | 20 | 1840.054 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1908.0776 | 1908.0558 | -0.07% | 1839.054 | 1 | 69.0018 | 77.8567 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+060.00 | 9855246.1315 | 779297.9037 | 1840.046 | 1060 | 20 | 1840.046 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1907.9077 | 1907.886 | -0.08% | 1839.046 | 1 | 68.84 | 77.8647 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+080.00 | 9855227.7448 | 779305.7731 | 1840.004 | 1080 | 20 | 1840.004 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1907.7379 | 1907.7161 | -0.25% | 1839.004 | 1 | 68.7121 | 77.9067 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+100.00 | 9855209.358 | 779313.6425 | 1839.944 | 1100 | 20 | 1839.944 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1907.568 | 1907.5462 | -0.51% | 1838.944 | 1 | 68.6022 | 77.9667 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+120.00 | 9855190.9712 | 779321.5119 | 1839.878 | 1120 | 20 | 1839.878 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1907.3981 | 1907.3764 | -0.63% | 1838.878 | 1 | 68.4984 | 78.0327 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+140.00 | 9855172.5845 | 779329.3813 | 1839.811 | 1140 | 20 | 1839.811 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1907.2283 | 1907.2065 | -0.665% | 1838.811 | 1 | 68.3955 | 78.0997 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+160.00 | 9855156.6886 | 779340.7167 | 1839.833 | 1160 | 20 | 1839.833 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1907.0584 | 1907.0366 | -0.225% | 1838.833 | 1 | 68.2036 | 78.0777 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+180.00 | 9855151.5044 | 779359.9691 | 1840.073 | 1180 | 20 | 1840.073 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1906.8885 | 1906.8668 | 1.31% | 1839.073 | 1 | 67.7938 | 77.8377 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+200.00 | 9855147.1021 | 779379.4786 | 1840.362 | 1200 | 20 | 1840.362 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1906.7187 | 1906.6969 | 2.645% | 1839.362 | 1 | 67.3349 | 77.5487 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+220.00 | 9855142.6998 | 779398.9881 | 1840.555 | 1220 | 20 | 1840.555 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1906.5488 | 1906.527 | 2.41% | 1839.555 | 1 | 66.972 | 77.3557 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+240.00 | 9855138.2974 | 779418.4975 | 1840.795 | 1240 | 20 | 1840.795 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1906.3789 | 1906.3572 | 2.165% | 1839.795 | 1 | 66.5622 | 77.1157 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+260.00 | 9855133.8951 | 779438.007 | 1841.041 | 1260 | 20 | 1841.041 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1906.2091 | 1906.1873 | 2.43% | 1840.041 | 1 | 66.1463 | 76.8697 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+280.00 | 9855129.4927 | 779457.5165 | 1841.271 | 1280 | 20 | 1841.271 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1906.0392 | 1906.0174 | 2.38% | 1840.271 | 1 | 65.7464 | 76.6397 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+300.00 | 9855125.0904 | 779477.026 | 1841.543 | 1300 | 20 | 1841.543 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1905.8693 | 1905.8476 | 2.51% | 1840.543 | 1 | 65.3046 | 76.3677 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+320.00 | 9855120.688 | 779496.5354 | 1841.875 | 1320 | 20 | 1841.875 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1905.6994 | 1905.6777 | 3.02% | 1840.875 | 1 | 64.8027 | 76.0357 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+340.00 | 9855116.2857 | 779516.0449 | 1842.174 | 1340 | 20 | 1842.174 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1905.5296 | 1905.5078 | 3.155% | 1841.174 | 1 | 64.3338 | 75.7367 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+360.00 | 9855111.8833 | 779535.5544 | 1842.458 | 1360 | 20 | 1842.458 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1905.3597 | 1905.338 | 2.915% | 1841.458 | 1 | 63.88 | 75.4527 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+380.00 | 9855107.481 | 779555.0638 | 1842.896 | 1380 | 20 | 1842.896 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1905.1898 | 1905.1681 | 3.61% | 1841.896 | 1 | 63.2721 | 75.0147 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+400.00 | 9855103.0787 | 779574.5733 | 1843.174 | 1400 | 20 | 1843.174 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1905.02 | 1904.9982 | 3.58% | 1842.174 | 1 | 62.8242 | 74.7367 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+420.00 | 9855098.6763 | 779594.0828 | 1843.45 | 1420 | 20 | 1843.45 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1904.8501 | 1904.8284 | 2.77% | 1842.45 | 1 | 62.3784 | 74.4607 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+440.00 | 9855094.274 | 779613.5922 | 1843.69 | 1440 | 20 | 1843.69 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1904.6802 | 1904.6585 | 2.58% | 1842.69 | 1 | 61.9685 | 74.2207 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+460.00 | 9855089.8716 | 779633.1017 | 1843.93 | 1460 | 20 | 1843.93 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1904.5104 | 1904.4886 | 2.4% | 1842.93 | 1 | 61.5586 | 73.9807 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+480.00 | 9855085.4693 | 779652.6112 | 1844.196 | 1480 | 20 | 1844.196 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1904.3405 | 1904.3187 | 2.53% | 1843.196 | 1 | 61.1227 | 73.7147 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+500.00 | 9855081.0669 | 779672.1206 | 1844.512 | 1500 | 20 | 1844.512 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1904.1706 | 1904.1489 | 2.91% | 1843.512 | 1 | 60.6369 | 73.3987 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+520.00 | 9855076.6646 | 779691.6301 | 1844.903 | 1520 | 20 | 1844.903 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1904.0008 | 1903.979 | 3.535% | 1843.903 | 1 | 60.076 | 73.0077 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+540.00 | 9855072.2623 | 779711.1396 | 1845.265 | 1540 | 20 | 1845.265 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1903.8309 | 1903.8091 | 3.765% | 1844.265 | 1 | 59.5441 | 72.6457 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+560.00 | 9855067.8599 | 779730.649 | 1845.544 | 1560 | 20 | 1845.544 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1903.661 | 1903.6393 | 3.205% | 1844.544 | 1 | 59.0953 | 72.3667 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+580.00 | 9855063.4576 | 779750.1585 | 1845.857 | 1580 | 20 | 1845.857 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1903.4912 | 1903.4694 | 2.96% | 1844.857 | 1 | 58.6124 | 72.0537 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+600.00 | 9855059.0552 | 779769.668 | 1846.188 | 1600 | 20 | 1846.188 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1903.3213 | 1903.2995 | 3.22% | 1845.188 | 1 | 58.1115 | 71.7227 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+620.00 | 9855054.6529 | 779789.1775 | 1846.484 | 1620 | 20 | 1846.484 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1903.1514 | 1903.1297 | 3.135% | 1845.484 | 1 | 57.6457 | 71.4267 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+640.00 | 9855050.2505 | 779808.6869 | 1846.874 | 1640 | 20 | 1846.874 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1902.9816 | 1902.9598 | 3.43% | 1845.874 | 1 | 57.0858 | 71.0367 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+660.00 | 9855045.8482 | 779828.1964 | 1847.366 | 1660 | 20 | 1847.366 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1902.8117 | 1902.7899 | 4.41% | 1846.366 | 1 | 56.4239 | 70.5447 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+680.00 | 9855041.4459 | 779847.7059 | 1847.862 | 1680 | 20 | 1847.862 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1902.6418 | 1902.6201 | 4.94% | 1846.862 | 1 | 55.7581 | 70.0487 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+700.00 | 9855037.0435 | 779867.2153 | 1848.259 | 1700 | 20 | 1848.259 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1902.472 | 1902.4502 | 4.465% | 1847.259 | 1 | 55.1912 | 69.6517 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+720.00 | 9855032.6412 | 779886.7248 | 1848.719 | 1720 | 20 | 1848.719 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1902.3021 | 1902.2803 | 4.285% | 1847.719 | 1 | 54.5613 | 69.1917 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+740.00 | 9855028.2388 | 779906.2343 | 1849.214 | 1740 | 20 | 1849.214 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1902.1322 | 1902.1105 | 4.775% | 1848.214 | 1 | 53.8965 | 68.6967 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+760.00 | 9855023.8365 | 779925.7437 | 1849.75 | 1760 | 20 | 1849.75 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1901.9624 | 1901.9406 | 5.155% | 1848.75 | 1 | 53.1906 | 68.1607 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+780.00 | 9855019.4341 | 779945.2532 | 1850.363 | 1780 | 20 | 1850.363 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1901.7925 | 1901.7707 | 5.745% | 1849.363 | 1 | 52.4077 | 67.5477 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+800.00 | 9855015.0318 | 779964.7627 | 1851.013 | 1800 | 20 | 1851.013 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1901.6226 | 1901.6009 | 6.315% | 1850.013 | 1 | 51.5879 | 66.8977 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+820.00 | 9855010.6294 | 779984.2721 | 1851.749 | 1820 | 20 | 1851.749 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1901.4527 | 1901.431 | 6.93% | 1850.749 | 1 | 50.682 | 66.1617 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+840.00 | 9855006.2271 | 780003.7816 | 1852.524 | 1840 | 20 | 1852.524 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1901.2829 | 1901.2611 | 7.555% | 1851.524 | 1 | 49.7371 | 65.3867 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+860.00 | 9855001.8248 | 780023.2911 | 1853.375 | 1860 | 20 | 1853.375 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1901.113 | 1901.0913 | 8.13% | 1852.375 | 1 | 48.7163 | 64.5357 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+880.00 | 9854997.4224 | 780042.8005 | 1854.313 | 1880 | 20 | 1854.313 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1900.9431 | 1900.9214 | 8.945% | 1853.313 | 1 | 47.6084 | 63.5977 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+900.00 | 9854993.0201 | 780062.31 | 1855.245 | 1900 | 20 | 1855.245 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1900.7733 | 1900.7515 | 9.35% | 1854.245 | 1 | 46.5065 | 62.6657 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+920.00 | 9854988.6177 | 780081.8195 | 1856.103 | 1920 | 20 | 1856.103 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1900.6034 | 1900.5817 | 8.95% | 1855.103 | 1 | 45.4787 | 61.8077 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+940.00 | 9854984.2154 | 780101.329 | 1856.924 | 1940 | 20 | 1856.924 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1900.4335 | 1900.4118 | 8.395% | 1855.924 | 1 | 44.4878 | 60.9867 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+960.00 | 9854979.813 | 780120.8384 | 1857.773 | 1960 | 20 | 1857.773 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1900.2637 | 1900.2419 | 8.35% | 1856.773 | 1 | 43.4689 | 60.1377 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+980.00 | 9854978.5594 | 780140.4557 | 1858.668 | 1980 | 20 | 1858.668 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1900.0938 | 1900.0721 | 8.72% | 1857.668 | 1 | 42.4041 | 59.2427 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+000.00 | 9854992.8627 | 780153.2307 | 1858.898 | 2000 | 20 | 1858.898 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1899.9239 | 1899.9022 | 5.625% | 1857.898 | 1 | 42.0042 | 59.0127 |  |  |  |  | Double Orifice ARV DN63 PN10 | 63 | 55.4 | 3.8 | PN 10.0
| 2+020.00 | 9855012.283 | 780158.0111 | 1858.867 | 2020 | 20 | 1858.867 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1899.7541 | 1899.7323 | 0.995% | 1857.867 | 1 | 41.8653 | 59.0437 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+040.00 | 9855031.7033 | 780162.7914 | 1858.918 | 2040 | 20 | 1858.918 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1899.5842 | 1899.5624 | 0.1% | 1857.918 | 1 | 41.6444 | 58.9927 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+060.00 | 9855051.1236 | 780167.5718 | 1858.911 | 2060 | 20 | 1858.911 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1899.4143 | 1899.3926 | 0.22% | 1857.911 | 1 | 41.4816 | 58.9997 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+080.00 | 9855070.544 | 780172.3521 | 1858.851 | 2080 | 20 | 1858.851 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1899.2445 | 1899.2227 | -0.335% | 1857.851 | 1 | 41.3717 | 59.0597 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+100.00 | 9855089.9643 | 780177.1325 | 1858.746 | 2100 | 20 | 1858.746 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1899.0746 | 1899.0528 | -0.825% | 1857.746 | 1 | 41.3068 | 59.1647 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+120.00 | 9855109.3846 | 780181.9129 | 1858.668 | 2120 | 20 | 1858.668 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1898.9047 | 1898.883 | -0.915% | 1857.668 | 1 | 41.215 | 59.2427 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+140.00 | 9855128.8049 | 780186.6932 | 1858.711 | 2140 | 20 | 1858.711 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1898.7349 | 1898.7131 | -0.175% | 1857.711 | 1 | 41.0021 | 59.1997 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+160.00 | 9855148.2252 | 780191.4736 | 1858.654 | 2160 | 20 | 1858.654 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1898.565 | 1898.5432 | -0.07% | 1857.654 | 1 | 40.8892 | 59.2567 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+180.00 | 9855167.6455 | 780196.2539 | 1858.678 | 2180 | 20 | 1858.678 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1898.3951 | 1898.3734 | -0.165% | 1857.678 | 1 | 40.6954 | 59.2327 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+200.00 | 9855187.0658 | 780201.0343 | 1858.651 | 2200 | 20 | 1858.651 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1898.2253 | 1898.2035 | -0.015% | 1857.651 | 1 | 40.5525 | 59.2597 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+220.00 | 9855206.4861 | 780205.8146 | 1858.774 | 2220 | 20 | 1858.774 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1898.0554 | 1898.0336 | 0.48% | 1857.774 | 1 | 40.2596 | 59.1367 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+240.00 | 9855225.9064 | 780210.595 | 1858.814 | 2240 | 20 | 1858.814 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1897.8855 | 1897.8638 | 0.815% | 1857.814 | 1 | 40.0498 | 59.0967 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+260.00 | 9855245.3267 | 780215.3753 | 1858.813 | 2260 | 20 | 1858.813 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1897.7157 | 1897.6939 | 0.195% | 1857.813 | 1 | 39.8809 | 59.0977 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+280.00 | 9855264.747 | 780220.1557 | 1858.761 | 2280 | 20 | 1858.761 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1897.5458 | 1897.524 | -0.265% | 1857.761 | 1 | 39.763 | 59.1497 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+300.00 | 9855284.1673 | 780224.936 | 1858.715 | 2300 | 20 | 1858.715 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1897.3759 | 1897.3542 | -0.49% | 1857.715 | 1 | 39.6392 | 59.1957 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+320.00 | 9855303.5876 | 780229.7164 | 1858.707 | 2320 | 20 | 1858.707 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1897.2061 | 1897.1843 | -0.27% | 1857.707 | 1 | 39.4773 | 59.2037 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+338.06 | 9855321.1233 | 780234.0329 | 1858.7 | 2340 | 20 | 1858.7 | 0.0015741 | 0.0554 | 0.0024093 | 0.65334 | 150 | 0.16987 | 0.021756 | 1916.9107 | 1897.0362 | 1897.0144 | -0.075% | 1857.7 | 1 | 39.3144 | 59.2107 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
19.8746

## Dist - Tank to WK1 to WK 3
ILMOCHIN WATER SUPPLY PROJECT
Contract No.: | [17 empty] | Soil Cover | 1 |  | Assumption: | Discharge | 0.00069444
Profile levels - end of line included
Date: 20.09.2022 | [27 empty] | Pipe Details
Nodes | Station | Northing (m) | Easting (m) | Elevation (m) | Chainage | Length (m) | Orig. Ground Level | Discharge (m3/s) | Internal diameter (m) | Area (m2) | Velocity (m/s) | C | HL | Vf | El Static | EL | HGL | Slope (%) | Pipe invert (m) | Depth of excavation (m) | Hp | Hs | Off-take (m3/s) | Total flow (m3/s) | Bends | Losses due to bends | Remarks | External Diameter (mm) | Internal Diameter (mm) | Wall Thickness (mm) | Class | Soil Type
| 0+000.00 | 9855321.0038 | 780234.5184 | 1858.717 | 0 | 0 | 1858.717 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0 | 0.025982 | 1859.217 | 1859.217 | 1859.191 |  | 1857.717 | 1 | 1.474 | 1.5 |  | 0.00069444 |  |  |  | 40 | 35.2 | 2.4 | PN10
| 0+020.00 | 9855301.5835 | 780229.738 | 1858.725 | 20 | 20 | 1858.725 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | 0.04% | 1857.725 | 1 | 1.466 | 1.492 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+040.00 | 9855282.1632 | 780224.9577 | 1858.734 | 40 | 20 | 1858.734 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | 0.045% | 1857.734 | 1 | 1.457 | 1.483 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+060.00 | 9855262.7429 | 780220.1773 | 1858.788 | 60 | 20 | 1858.788 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | 0.27% | 1857.788 | 1 | 1.403 | 1.429 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+080.00 | 9855243.3226 | 780215.3969 | 1858.832 | 80 | 20 | 1858.832 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | 0.22% | 1857.832 | 1 | 1.359 | 1.385 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+100.00 | 9855223.9023 | 780210.6166 | 1858.828 | 100 | 20 | 1858.828 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -0.02% | 1857.828 | 1 | 1.363 | 1.389 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+120.00 | 9855204.482 | 780205.8362 | 1858.785 | 120 | 20 | 1858.785 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -0.215% | 1857.785 | 1 | 1.406 | 1.432 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+140.00 | 9855185.0617 | 780201.0559 | 1858.671 | 140 | 20 | 1858.671 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -0.57% | 1857.671 | 1 | 1.52 | 1.546 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+160.00 | 9855165.6414 | 780196.2755 | 1858.676 | 160 | 20 | 1858.676 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | 0.025% | 1857.676 | 1 | 1.515 | 1.541 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+180.00 | 9855146.2211 | 780191.4952 | 1858.661 | 180 | 20 | 1858.661 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -0.075% | 1857.661 | 1 | 1.53 | 1.556 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+200.00 | 9855126.8008 | 780186.7148 | 1858.717 | 200 | 20 | 1858.717 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | 0.28% | 1857.717 | 1 | 1.474 | 1.5 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+220.00 | 9855107.3805 | 780181.9345 | 1858.709 | 220 | 20 | 1858.709 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -0.04% | 1857.709 | 1 | 1.482 | 1.508 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+240.00 | 9855087.9602 | 780177.1541 | 1858.769 | 240 | 20 | 1858.769 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | 0.3% | 1857.769 | 1 | 1.422 | 1.448 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+260.00 | 9855068.5399 | 780172.3738 | 1858.864 | 260 | 20 | 1858.864 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | 0.475% | 1857.864 | 1 | 1.327 | 1.353 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+280.00 | 9855049.1196 | 780167.5934 | 1858.916 | 280 | 20 | 1858.916 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | 0.26% | 1857.916 | 1 | 1.275 | 1.301 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+300.00 | 9855029.6993 | 780162.813 | 1858.952 | 300 | 20 | 1858.952 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | 0.18% | 1857.952 | 1 | 1.239 | 1.265 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+320.00 | 9855010.2789 | 780158.0327 | 1858.877 | 320 | 20 | 1858.877 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -0.375% | 1857.877 | 1 | 1.314 | 1.34 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+340.00 | 9854990.8567 | 780153.2602 | 1858.909 | 340 | 20 | 1858.909 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | 0.16% | 1857.909 | 1 | 1.282 | 1.308 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+360.00 | 9854974.5589 | 780144.1818 | 1858.846 | 360 | 20 | 1858.846 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -0.315% | 1857.846 | 1 | 1.345 | 1.371 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+380.00 | 9854978.3397 | 780124.6181 | 1857.919 | 380 | 20 | 1857.919 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -4.635% | 1856.919 | 1 | 2.272 | 2.298 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+400.00 | 9854982.7618 | 780105.1131 | 1857.073 | 400 | 20 | 1857.073 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -4.23% | 1856.073 | 1 | 3.118 | 3.144 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+420.00 | 9854987.1839 | 780085.6081 | 1856.257 | 420 | 20 | 1856.257 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -4.08% | 1855.257 | 1 | 3.934 | 3.96 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+440.00 | 9854991.606 | 780066.1031 | 1855.428 | 440 | 20 | 1855.428 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -4.145% | 1854.428 | 1 | 4.763 | 4.789 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+460.00 | 9854996.028 | 780046.5981 | 1854.504 | 460 | 20 | 1854.504 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -4.62% | 1853.504 | 1 | 5.687 | 5.713 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+480.00 | 9855000.4501 | 780027.093 | 1853.555 | 480 | 20 | 1853.555 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -4.745% | 1852.555 | 1 | 6.636 | 6.662 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+500.00 | 9855004.8564 | 780007.5845 | 1852.703 | 500 | 20 | 1852.703 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -4.26% | 1851.703 | 1 | 7.488 | 7.514 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+520.00 | 9855009.2588 | 779988.075 | 1851.928 | 520 | 20 | 1851.928 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -3.875% | 1850.928 | 1 | 8.263 | 8.289 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+540.00 | 9855013.6611 | 779968.5655 | 1851.172 | 540 | 20 | 1851.172 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -3.78% | 1850.172 | 1 | 9.019 | 9.045 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+560.00 | 9855018.0634 | 779949.0561 | 1850.558 | 560 | 20 | 1850.558 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -3.07% | 1849.558 | 1 | 9.633 | 9.659 | 0 |  |  |  |  | 40 | 35.2 | 2.4 | PN10
| 0+580.00 | 9855022.4658 | 779929.5466 | 1849.943 | 580 | 20 | 1849.943 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -3.075% | 1848.943 | 1 | 10.248 | 10.274 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+600.00 | 9855026.8681 | 779910.0371 | 1849.367 | 600 | 20 | 1849.367 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -2.88% | 1848.367 | 1 | 10.824 | 10.85 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+620.00 | 9855031.2705 | 779890.5277 | 1848.804 | 620 | 20 | 1848.804 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -2.815% | 1847.804 | 1 | 11.387 | 11.413 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+640.00 | 9855035.6728 | 779871.0182 | 1848.344 | 640 | 20 | 1848.344 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -2.3% | 1847.344 | 1 | 11.847 | 11.873 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+660.00 | 9855040.0752 | 779851.5087 | 1847.933 | 660 | 20 | 1847.933 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -2.055% | 1846.933 | 1 | 12.258 | 12.284 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+680.00 | 9855044.4775 | 779831.9993 | 1847.47 | 680 | 20 | 1847.47 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -2.315% | 1846.47 | 1 | 12.721 | 12.747 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+700.00 | 9855048.8798 | 779812.4898 | 1846.945 | 700 | 20 | 1846.945 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -2.625% | 1845.945 | 1 | 13.246 | 13.272 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+720.00 | 9855053.2822 | 779792.9803 | 1846.555 | 720 | 20 | 1846.555 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -1.95% | 1845.555 | 1 | 13.636 | 13.662 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+740.00 | 9855057.6845 | 779773.4709 | 1846.238 | 740 | 20 | 1846.238 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -1.585% | 1845.238 | 1 | 13.953 | 13.979 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+760.00 | 9855062.0869 | 779753.9614 | 1845.919 | 760 | 20 | 1845.919 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -1.595% | 1844.919 | 1 | 14.272 | 14.298 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+780.00 | 9855066.4892 | 779734.4519 | 1845.585 | 780 | 20 | 1845.585 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -1.67% | 1844.585 | 1 | 14.606 | 14.632 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+800.00 | 9855070.8916 | 779714.9424 | 1845.327 | 800 | 20 | 1845.327 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -1.29% | 1844.327 | 1 | 14.864 | 14.89 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+820.00 | 9855075.2939 | 779695.433 | 1844.968 | 820 | 20 | 1844.968 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -1.795% | 1843.968 | 1 | 15.223 | 15.249 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+840.00 | 9855079.6964 | 779675.9235 | 1844.624 | 840 | 20 | 1844.624 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -1.72% | 1843.624 | 1 | 15.567 | 15.593 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+860.00 | 9855084.0988 | 779656.4141 | 1844.271 | 860 | 20 | 1844.271 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -1.765% | 1843.271 | 1 | 15.92 | 15.946 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+880.00 | 9855088.5013 | 779636.9047 | 1843.99 | 880 | 20 | 1843.99 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -1.405% | 1842.99 | 1 | 16.201 | 16.227 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+900.00 | 9855092.9038 | 779617.3952 | 1843.75 | 900 | 20 | 1843.75 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -1.2% | 1842.75 | 1 | 16.441 | 16.467 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+920.00 | 9855097.3063 | 779597.8858 | 1843.511 | 920 | 20 | 1843.511 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -1.195% | 1842.511 | 1 | 16.68 | 16.706 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+940.00 | 9855101.7088 | 779578.3763 | 1843.248 | 940 | 20 | 1843.248 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -1.315% | 1842.248 | 1 | 16.943 | 16.969 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+960.00 | 9855106.1113 | 779558.8669 | 1842.985 | 960 | 20 | 1842.985 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -1.315% | 1841.985 | 1 | 17.206 | 17.232 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 0+980.00 | 9855110.5138 | 779539.3575 | 1842.576 | 980 | 20 | 1842.576 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -2.045% | 1841.576 | 1 | 17.615 | 17.641 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+000.00 | 9855114.9163 | 779519.848 | 1842.24 | 1000 | 20 | 1842.24 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -1.68% | 1841.24 | 1 | 17.951 | 17.977 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+020.00 | 9855119.3187 | 779500.3386 | 1841.973 | 1020 | 20 | 1841.973 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -1.335% | 1840.973 | 1 | 18.218 | 18.244 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+040.00 | 9855123.7212 | 779480.8292 | 1841.617 | 1040 | 20 | 1841.617 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -1.78% | 1840.617 | 1 | 18.574 | 18.6 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+060.00 | 9855128.1237 | 779461.3197 | 1841.345 | 1060 | 20 | 1841.345 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -1.36% | 1840.345 | 1 | 18.846 | 18.872 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+080.00 | 9855132.5262 | 779441.8103 | 1841.105 | 1080 | 20 | 1841.105 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -1.2% | 1840.105 | 1 | 19.086 | 19.112 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+100.00 | 9855136.9287 | 779422.3009 | 1840.866 | 1100 | 20 | 1840.866 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -1.195% | 1839.866 | 1 | 19.325 | 19.351 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+120.00 | 9855141.3312 | 779402.7914 | 1840.609 | 1120 | 20 | 1840.609 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -1.285% | 1839.609 | 1 | 19.582 | 19.608 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+140.00 | 9855145.7337 | 779383.282 | 1840.422 | 1140 | 20 | 1840.422 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -0.935% | 1839.422 | 1 | 19.769 | 19.795 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+160.00 | 9855150.1361 | 779363.7725 | 1840.152 | 1160 | 20 | 1840.152 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -1.35% | 1839.152 | 1 | 20.039 | 20.065 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+180.00 | 9855154.5386 | 779344.2631 | 1839.891 | 1180 | 20 | 1839.891 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -1.305% | 1838.891 | 1 | 20.3 | 20.326 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+200.00 | 9855167.4533 | 779331.0698 | 1839.78 | 1200 | 20 | 1839.78 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -0.555% | 1838.78 | 1 | 20.411 | 20.437 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+220.00 | 9855185.8341 | 779323.1867 | 1839.843 | 1220 | 20 | 1839.843 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | 0.315% | 1838.843 | 1 | 20.348 | 20.374 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+240.00 | 9855204.2307 | 779315.3404 | 1839.912 | 1240 | 20 | 1839.912 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | 0.345% | 1838.912 | 1 | 20.279 | 20.305 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+260.00 | 9855222.6274 | 779307.4942 | 1839.976 | 1260 | 20 | 1839.976 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | 0.32% | 1838.976 | 1 | 20.215 | 20.241 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+280.00 | 9855241.024 | 779299.6479 | 1840.025 | 1280 | 20 | 1840.025 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | 0.245% | 1839.025 | 1 | 20.166 | 20.192 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+300.00 | 9855259.4207 | 779291.8017 | 1840.052 | 1300 | 20 | 1840.052 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | 0.135% | 1839.052 | 1 | 20.139 | 20.165 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+320.00 | 9855277.8173 | 779283.9554 | 1840.053 | 1320 | 20 | 1840.053 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | 0.005% | 1839.053 | 1 | 20.138 | 20.164 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+340.00 | 9855296.2139 | 779276.1091 | 1840.064 | 1340 | 20 | 1840.064 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | 0.055% | 1839.064 | 1 | 20.127 | 20.153 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+360.00 | 9855314.6106 | 779268.2629 | 1840.063 | 1360 | 20 | 1840.063 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -0.005% | 1839.063 | 1 | 20.128 | 20.154 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+380.00 | 9855333.0072 | 779260.4166 | 1840.05 | 1380 | 20 | 1840.05 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -0.065% | 1839.05 | 1 | 20.141 | 20.167 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+400.00 | 9855351.4038 | 779252.5703 | 1840.03 | 1400 | 20 | 1840.03 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -0.1% | 1839.03 | 1 | 20.161 | 20.187 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+420.00 | 9855369.8005 | 779244.7241 | 1840.037 | 1420 | 20 | 1840.037 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | 0.035% | 1839.037 | 1 | 20.154 | 20.18 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+440.00 | 9855388.1971 | 779236.8778 | 1840.067 | 1440 | 20 | 1840.067 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | 0.15% | 1839.067 | 1 | 20.124 | 20.15 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+460.00 | 9855406.5937 | 779229.0316 | 1840.046 | 1460 | 20 | 1840.046 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -0.105% | 1839.046 | 1 | 20.145 | 20.171 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+480.00 | 9855424.9904 | 779221.1853 | 1840.026 | 1480 | 20 | 1840.026 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -0.1% | 1839.026 | 1 | 20.165 | 20.191 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+500.00 | 9855443.387 | 779213.339 | 1840.07 | 1500 | 20 | 1840.07 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | 0.22% | 1839.07 | 1 | 20.121 | 20.147 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+520.00 | 9855461.7836 | 779205.4928 | 1840.082 | 1520 | 20 | 1840.082 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | 0.06% | 1839.082 | 1 | 20.109 | 20.135 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+540.00 | 9855480.1803 | 779197.6465 | 1840.06 | 1540 | 20 | 1840.06 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -0.11% | 1839.06 | 1 | 20.131 | 20.157 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+560.00 | 9855498.5769 | 779189.8003 | 1840.035 | 1560 | 20 | 1840.035 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -0.125% | 1839.035 | 1 | 20.156 | 20.182 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+580.00 | 9855516.9735 | 779181.954 | 1840.022 | 1580 | 20 | 1840.022 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -0.065% | 1839.022 | 1 | 20.169 | 20.195 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+600.00 | 9855535.3702 | 779174.1077 | 1840.019 | 1600 | 20 | 1840.019 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -0.015% | 1839.019 | 1 | 20.172 | 20.198 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+620.00 | 9855553.7668 | 779166.2615 | 1840.022 | 1620 | 20 | 1840.022 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | 0.015% | 1839.022 | 1 | 20.169 | 20.195 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+640.00 | 9855572.1635 | 779158.4152 | 1840.009 | 1640 | 20 | 1840.009 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -0.065% | 1839.009 | 1 | 20.182 | 20.208 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+660.00 | 9855590.5601 | 779150.569 | 1839.968 | 1660 | 20 | 1839.968 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -0.205% | 1838.968 | 1 | 20.223 | 20.249 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+680.00 | 9855608.9567 | 779142.7227 | 1839.923 | 1680 | 20 | 1839.923 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -0.225% | 1838.923 | 1 | 20.268 | 20.294 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+700.00 | 9855627.3534 | 779134.8764 | 1839.898 | 1700 | 20 | 1839.898 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -0.125% | 1838.898 | 1 | 20.293 | 20.319 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+720.00 | 9855645.75 | 779127.0302 | 1839.867 | 1720 | 20 | 1839.867 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -0.155% | 1838.867 | 1 | 20.324 | 20.35 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+740.00 | 9855664.1466 | 779119.1839 | 1839.806 | 1740 | 20 | 1839.806 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -0.305% | 1838.806 | 1 | 20.385 | 20.411 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+760.00 | 9855682.5433 | 779111.3377 | 1839.791 | 1760 | 20 | 1839.791 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -0.075% | 1838.791 | 1 | 20.4 | 20.426 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+780.00 | 9855700.9399 | 779103.4914 | 1839.756 | 1780 | 20 | 1839.756 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -0.175% | 1838.756 | 1 | 20.435 | 20.461 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+800.00 | 9855719.3365 | 779095.6451 | 1839.695 | 1800 | 20 | 1839.695 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -0.305% | 1838.695 | 1 | 20.496 | 20.522 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+820.00 | 9855737.7332 | 779087.7989 | 1839.639 | 1820 | 20 | 1839.639 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -0.28% | 1838.639 | 1 | 20.552 | 20.578 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+840.00 | 9855756.1298 | 779079.9526 | 1839.544 | 1840 | 20 | 1839.544 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -0.475% | 1838.544 | 1 | 20.647 | 20.673 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+860.00 | 9855774.5264 | 779072.1064 | 1839.465 | 1860 | 20 | 1839.465 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -0.395% | 1838.465 | 1 | 20.726 | 20.752 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+880.00 | 9855792.9332 | 779064.284 | 1839.299 | 1880 | 20 | 1839.299 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -0.83% | 1838.299 | 1 | 20.892 | 20.918 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+900.00 | 9855806.608 | 779049.8975 | 1839.071 | 1900 | 20 | 1839.071 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -1.14% | 1838.071 | 1 | 21.12 | 21.146 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+920.00 | 9855819.7037 | 779034.7813 | 1838.826 | 1920 | 20 | 1838.826 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -1.225% | 1837.826 | 1 | 21.365 | 21.391 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+940.00 | 9855832.7995 | 779019.665 | 1838.559 | 1940 | 20 | 1838.559 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -1.335% | 1837.559 | 1 | 21.632 | 21.658 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+960.00 | 9855845.8953 | 779004.5488 | 1838.324 | 1960 | 20 | 1838.324 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -1.175% | 1837.324 | 1 | 21.867 | 21.893 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 1+980.00 | 9855858.991 | 778989.4325 | 1838.111 | 1980 | 20 | 1838.111 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -1.065% | 1837.111 | 1 | 22.08 | 22.106 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+000.00 | 9855872.0868 | 778974.3163 | 1837.878 | 2000 | 20 | 1837.878 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.33991 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -1.165% | 1836.878 | 1 | 22.313 | 22.339 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+007.21 | 9855876.8066 | 778968.8682 | 1837.787 | 2007.21 | 7.21 | 1837.787 | 0.00069444 | 0.0352 | 0.00097265 | 0.71397 | 150 | 0.12254 | 0.025982 | 1859.217 | 1859.217 | 1859.191 | -1.262% | 1836.787 | 1 | 22.404 | 22.43 | 0.00023148 |  |  |  | Water Kiosk at Ilmochin Primary | 40 | 35.2 | 2.4 | PN10
| 2+020.00 | 9855890.5696 | 778954.3482 | 1837.587 | 2020 | 12.79 | 1837.587 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.10258 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.564% | 1836.587 | 1 | 22.6185 | 22.63 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+040.00 | 9855903.9612 | 778939.4934 | 1837.417 | 2040 | 20 | 1837.417 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -0.85% | 1836.417 | 1 | 22.7885 | 22.8 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+060.00 | 9855917.3527 | 778924.6385 | 1837.134 | 2060 | 20 | 1837.134 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.415% | 1836.134 | 1 | 23.0715 | 23.083 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+080.00 | 9855930.7443 | 778909.7837 | 1836.883 | 2080 | 20 | 1836.883 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.255% | 1835.883 | 1 | 23.3225 | 23.334 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+100.00 | 9855944.1359 | 778894.9289 | 1836.662 | 2100 | 20 | 1836.662 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.105% | 1835.662 | 1 | 23.5435 | 23.555 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+120.00 | 9855957.5275 | 778880.0741 | 1836.449 | 2120 | 20 | 1836.449 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.065% | 1835.449 | 1 | 23.7565 | 23.768 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+140.00 | 9855970.919 | 778865.2193 | 1836.254 | 2140 | 20 | 1836.254 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -0.975% | 1835.254 | 1 | 23.9515 | 23.963 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+160.00 | 9855984.3106 | 778850.3644 | 1836.022 | 2160 | 20 | 1836.022 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.16% | 1835.022 | 1 | 24.1835 | 24.195 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+180.00 | 9855997.7022 | 778835.5096 | 1835.753 | 2180 | 20 | 1835.753 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.345% | 1834.753 | 1 | 24.4525 | 24.464 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+200.00 | 9856011.0938 | 778820.6548 | 1835.47 | 2200 | 20 | 1835.47 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.415% | 1834.47 | 1 | 24.7355 | 24.747 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+220.00 | 9856024.4854 | 778805.8 | 1835.216 | 2220 | 20 | 1835.216 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.27% | 1834.216 | 1 | 24.9895 | 25.001 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+240.00 | 9856037.8769 | 778790.9452 | 1834.996 | 2240 | 20 | 1834.996 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.1% | 1833.996 | 1 | 25.2095 | 25.221 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+260.00 | 9856051.2685 | 778776.0903 | 1834.775 | 2260 | 20 | 1834.775 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.105% | 1833.775 | 1 | 25.4305 | 25.442 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+280.00 | 9856064.6601 | 778761.2355 | 1834.514 | 2280 | 20 | 1834.514 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.305% | 1833.514 | 1 | 25.6915 | 25.703 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+300.00 | 9856078.0517 | 778746.3807 | 1834.196 | 2300 | 20 | 1834.196 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.59% | 1833.196 | 1 | 26.0095 | 26.021 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+320.00 | 9856091.4432 | 778731.5259 | 1834.056 | 2320 | 20 | 1834.056 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -0.7% | 1833.056 | 1 | 26.1495 | 26.161 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+340.00 | 9856104.8348 | 778716.6711 | 1833.826 | 2340 | 20 | 1833.826 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.15% | 1832.826 | 1 | 26.3795 | 26.391 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+360.00 | 9856118.2264 | 778701.8163 | 1833.519 | 2360 | 20 | 1833.519 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.535% | 1832.519 | 1 | 26.6865 | 26.698 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+380.00 | 9856131.618 | 778686.9614 | 1833.258 | 2380 | 20 | 1833.258 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.305% | 1832.258 | 1 | 26.9475 | 26.959 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+400.00 | 9856145.0095 | 778672.1066 | 1832.937 | 2400 | 20 | 1832.937 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.605% | 1831.937 | 1 | 27.2685 | 27.28 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+420.00 | 9856158.4011 | 778657.2518 | 1832.676 | 2420 | 20 | 1832.676 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.305% | 1831.676 | 1 | 27.5295 | 27.541 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+440.00 | 9856171.7927 | 778642.397 | 1832.435 | 2440 | 20 | 1832.435 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.205% | 1831.435 | 1 | 27.7705 | 27.782 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+460.00 | 9856185.1843 | 778627.5422 | 1832.211 | 2460 | 20 | 1832.211 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.12% | 1831.211 | 1 | 27.9945 | 28.006 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+480.00 | 9856198.5759 | 778612.6873 | 1831.982 | 2480 | 20 | 1831.982 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.145% | 1830.982 | 1 | 28.2235 | 28.235 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+500.00 | 9856211.9674 | 778597.8325 | 1831.753 | 2500 | 20 | 1831.753 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.145% | 1830.753 | 1 | 28.4525 | 28.464 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+520.00 | 9856225.359 | 778582.9777 | 1831.462 | 2520 | 20 | 1831.462 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.455% | 1830.462 | 1 | 28.7435 | 28.755 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+540.00 | 9856238.7506 | 778568.1229 | 1831.148 | 2540 | 20 | 1831.148 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.57% | 1830.148 | 1 | 29.0575 | 29.069 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+560.00 | 9856252.1422 | 778553.2681 | 1830.871 | 2560 | 20 | 1830.871 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.385% | 1829.871 | 1 | 29.3345 | 29.346 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+580.00 | 9856265.5337 | 778538.4132 | 1830.698 | 2580 | 20 | 1830.698 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -0.865% | 1829.698 | 1 | 29.5075 | 29.519 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+600.00 | 9856278.9253 | 778523.5584 | 1830.436 | 2600 | 20 | 1830.436 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.31% | 1829.436 | 1 | 29.7695 | 29.781 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+620.00 | 9856292.3169 | 778508.7036 | 1830.21 | 2620 | 20 | 1830.21 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.13% | 1829.21 | 1 | 29.9955 | 30.007 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+640.00 | 9856305.7085 | 778493.8488 | 1829.976 | 2640 | 20 | 1829.976 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.17% | 1828.976 | 1 | 30.2295 | 30.241 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+660.00 | 9856319.1001 | 778478.994 | 1829.753 | 2660 | 20 | 1829.753 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.115% | 1828.753 | 1 | 30.4525 | 30.464 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+680.00 | 9856332.4916 | 778464.1391 | 1829.585 | 2680 | 20 | 1829.585 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -0.84% | 1828.585 | 1 | 30.6205 | 30.632 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+700.00 | 9856345.8832 | 778449.2843 | 1829.356 | 2700 | 20 | 1829.356 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.145% | 1828.356 | 1 | 30.8495 | 30.861 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+720.00 | 9856359.2748 | 778434.4295 | 1829.113 | 2720 | 20 | 1829.113 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.215% | 1828.113 | 1 | 31.0925 | 31.104 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+740.00 | 9856372.6664 | 778419.5747 | 1828.869 | 2740 | 20 | 1828.869 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.22% | 1827.869 | 1 | 31.3365 | 31.348 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+760.00 | 9856386.0579 | 778404.7199 | 1828.64 | 2760 | 20 | 1828.64 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.145% | 1827.64 | 1 | 31.5655 | 31.577 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+780.00 | 9856399.4495 | 778389.865 | 1828.407 | 2780 | 20 | 1828.407 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.165% | 1827.407 | 1 | 31.7985 | 31.81 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+800.00 | 9856412.8411 | 778375.0102 | 1828.184 | 2800 | 20 | 1828.184 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.115% | 1827.184 | 1 | 32.0215 | 32.033 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+820.00 | 9856427.5343 | 778361.9741 | 1827.944 | 2820 | 20 | 1827.944 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.2% | 1826.944 | 1 | 32.2615 | 32.273 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+840.00 | 9856443.5089 | 778372.0339 | 1827.882 | 2840 | 20 | 1827.882 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -0.31% | 1826.882 | 1 | 32.3235 | 32.335 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+860.00 | 9856456.8302 | 778386.9517 | 1827.919 | 2860 | 20 | 1827.919 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 0.185% | 1826.919 | 1 | 32.2865 | 32.298 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+880.00 | 9856470.1516 | 778401.8696 | 1827.875 | 2880 | 20 | 1827.875 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -0.22% | 1826.875 | 1 | 32.3305 | 32.342 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+900.00 | 9856483.4729 | 778416.7874 | 1827.69 | 2900 | 20 | 1827.69 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -0.925% | 1826.69 | 1 | 32.5155 | 32.527 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+920.00 | 9856496.7942 | 778431.7053 | 1827.424 | 2920 | 20 | 1827.424 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.33% | 1826.424 | 1 | 32.7815 | 32.793 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+940.00 | 9856510.1155 | 778446.6231 | 1827.279 | 2940 | 20 | 1827.279 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -0.725% | 1826.279 | 1 | 32.9265 | 32.938 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+960.00 | 9856523.4369 | 778461.541 | 1827.059 | 2960 | 20 | 1827.059 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.1% | 1826.059 | 1 | 33.1465 | 33.158 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 2+980.00 | 9856536.7582 | 778476.4588 | 1826.831 | 2980 | 20 | 1826.831 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -1.14% | 1825.831 | 1 | 33.3745 | 33.386 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+000.00 | 9856550.0795 | 778491.3767 | 1826.676 | 3000 | 20 | 1826.676 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -0.775% | 1825.676 | 1 | 33.5295 | 33.541 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+020.00 | 9856563.5535 | 778506.1442 | 1826.711 | 3020 | 20 | 1826.711 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 0.175% | 1825.711 | 1 | 33.4945 | 33.506 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+040.00 | 9856580.0444 | 778517.4548 | 1826.849 | 3040 | 20 | 1826.849 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 0.69% | 1825.849 | 1 | 33.3565 | 33.368 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+060.00 | 9856596.5933 | 778528.6857 | 1827.056 | 3060 | 20 | 1827.056 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 1.035% | 1826.056 | 1 | 33.1495 | 33.161 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+080.00 | 9856613.1422 | 778539.9166 | 1827.285 | 3080 | 20 | 1827.285 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 1.145% | 1826.285 | 1 | 32.9205 | 32.932 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+100.00 | 9856629.7232 | 778551.0991 | 1827.503 | 3100 | 20 | 1827.503 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 1.09% | 1826.503 | 1 | 32.7025 | 32.714 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+120.00 | 9856646.5218 | 778561.953 | 1827.653 | 3120 | 20 | 1827.653 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 0.75% | 1826.653 | 1 | 32.5525 | 32.564 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+140.00 | 9856663.3204 | 778572.807 | 1827.918 | 3140 | 20 | 1827.918 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 1.325% | 1826.918 | 1 | 32.2875 | 32.299 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+160.00 | 9856680.119 | 778583.6609 | 1828.197 | 3160 | 20 | 1828.197 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 1.395% | 1827.197 | 1 | 32.0085 | 32.02 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+180.00 | 9856696.9175 | 778594.5148 | 1828.464 | 3180 | 20 | 1828.464 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 1.335% | 1827.464 | 1 | 31.7415 | 31.753 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+200.00 | 9856713.7161 | 778605.3688 | 1828.755 | 3200 | 20 | 1828.755 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 1.455% | 1827.755 | 1 | 31.4505 | 31.462 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+220.00 | 9856730.5147 | 778616.2227 | 1829.203 | 3220 | 20 | 1829.203 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 2.24% | 1828.203 | 1 | 31.0025 | 31.014 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+240.00 | 9856747.3133 | 778627.0766 | 1829.329 | 3240 | 20 | 1829.329 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 0.63% | 1828.329 | 1 | 30.8765 | 30.888 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+260.00 | 9856763.9919 | 778638.1118 | 1829.458 | 3260 | 20 | 1829.458 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 0.645% | 1828.458 | 1 | 30.7475 | 30.759 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+280.00 | 9856780.5473 | 778649.3331 | 1829.627 | 3280 | 20 | 1829.627 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 0.845% | 1828.627 | 1 | 30.5785 | 30.59 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+300.00 | 9856797.1028 | 778660.5544 | 1829.796 | 3300 | 20 | 1829.796 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 0.845% | 1828.796 | 1 | 30.4095 | 30.421 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+320.00 | 9856813.6582 | 778671.7757 | 1830.029 | 3320 | 20 | 1830.029 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 1.165% | 1829.029 | 1 | 30.1765 | 30.188 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+340.00 | 9856830.2136 | 778682.997 | 1830.277 | 3340 | 20 | 1830.277 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 1.24% | 1829.277 | 1 | 29.9285 | 29.94 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+360.00 | 9856846.7691 | 778694.2183 | 1830.492 | 3360 | 20 | 1830.492 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 1.075% | 1829.492 | 1 | 29.7135 | 29.725 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+380.00 | 9856863.3245 | 778705.4396 | 1830.667 | 3380 | 20 | 1830.667 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 0.875% | 1829.667 | 1 | 29.5385 | 29.55 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+400.00 | 9856879.8799 | 778716.661 | 1830.868 | 3400 | 20 | 1830.868 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 1.005% | 1829.868 | 1 | 29.3375 | 29.349 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+420.00 | 9856896.4353 | 778727.8823 | 1831.083 | 3420 | 20 | 1831.083 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 1.075% | 1830.083 | 1 | 29.1225 | 29.134 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+440.00 | 9856912.9908 | 778739.1036 | 1831.016 | 3440 | 20 | 1831.016 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -0.335% | 1830.016 | 1 | 29.1895 | 29.201 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+460.00 | 9856929.5462 | 778750.3249 | 1830.922 | 3460 | 20 | 1830.922 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -0.47% | 1829.922 | 1 | 29.2835 | 29.295 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+480.00 | 9856946.1016 | 778761.5462 | 1831.08 | 3480 | 20 | 1831.08 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 0.79% | 1830.08 | 1 | 29.1255 | 29.137 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+500.00 | 9856962.657 | 778772.7675 | 1831.061 | 3500 | 20 | 1831.061 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -0.095% | 1830.061 | 1 | 29.1445 | 29.156 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+520.00 | 9856979.2125 | 778783.9888 | 1831.017 | 3520 | 20 | 1831.017 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -0.22% | 1830.017 | 1 | 29.1885 | 29.2 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+540.00 | 9856995.7679 | 778795.2101 | 1830.998 | 3540 | 20 | 1830.998 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -0.095% | 1829.998 | 1 | 29.2075 | 29.219 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+560.00 | 9857012.3233 | 778806.4314 | 1830.997 | 3560 | 20 | 1830.997 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | -0.005% | 1829.997 | 1 | 29.2085 | 29.22 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+580.00 | 9857028.8788 | 778817.6528 | 1831.031 | 3580 | 20 | 1831.031 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 0.17% | 1830.031 | 1 | 29.1745 | 29.186 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+600.00 | 9857045.5808 | 778828.654 | 1831.115 | 3600 | 20 | 1831.115 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 0.42% | 1830.115 | 1 | 29.0905 | 29.102 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+620.00 | 9857062.3115 | 778839.6123 | 1831.258 | 3620 | 20 | 1831.258 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 0.715% | 1830.258 | 1 | 28.9475 | 28.959 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+640.00 | 9857079.0421 | 778850.5707 | 1831.382 | 3640 | 20 | 1831.382 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 0.62% | 1830.382 | 1 | 28.8235 | 28.835 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+660.00 | 9857095.7727 | 778861.5291 | 1831.604 | 3660 | 20 | 1831.604 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 1.11% | 1830.604 | 1 | 28.6015 | 28.613 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+680.00 | 9857112.5034 | 778872.4875 | 1831.894 | 3680 | 20 | 1831.894 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 1.45% | 1830.894 | 1 | 28.3115 | 28.323 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+700.00 | 9857129.234 | 778883.4458 | 1832.186 | 3700 | 20 | 1832.186 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 1.46% | 1831.186 | 1 | 28.0195 | 28.031 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+720.00 | 9857145.9646 | 778894.4042 | 1832.515 | 3720 | 20 | 1832.515 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 1.645% | 1831.515 | 1 | 27.6905 | 27.702 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+740.00 | 9857162.6953 | 778905.3626 | 1832.681 | 3740 | 20 | 1832.681 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 0.83% | 1831.681 | 1 | 27.5245 | 27.536 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+760.00 | 9857179.4259 | 778916.321 | 1832.819 | 3760 | 20 | 1832.819 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 0.69% | 1831.819 | 1 | 27.3865 | 27.398 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+780.00 | 9857196.1565 | 778927.2793 | 1832.955 | 3780 | 20 | 1832.955 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 0.68% | 1831.955 | 1 | 27.2505 | 27.262 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+800.00 | 9857212.8872 | 778938.2377 | 1833.126 | 3800 | 20 | 1833.126 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 0.855% | 1832.126 | 1 | 27.0795 | 27.091 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+820.00 | 9857229.6178 | 778949.1961 | 1833.329 | 3820 | 20 | 1833.329 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 1.015% | 1832.329 | 1 | 26.8765 | 26.888 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+840.00 | 9857242.5141 | 778963.7863 | 1833.522 | 3840 | 20 | 1833.522 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 0.965% | 1832.522 | 1 | 26.6835 | 26.695 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+860.00 | 9857250.107 | 778982.2889 | 1833.773 | 3860 | 20 | 1833.773 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 1.255% | 1832.773 | 1 | 26.4325 | 26.444 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+880.00 | 9857257.6998 | 779000.7916 | 1834.097 | 3880 | 20 | 1834.097 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 1.62% | 1833.097 | 1 | 26.1085 | 26.12 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+900.00 | 9857265.2927 | 779019.2943 | 1834.356 | 3900 | 20 | 1834.356 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 1.295% | 1833.356 | 1 | 25.8495 | 25.861 | [5 empty] | 40 | 35.2 | 2.4 | PN10
| 3+902.45 | 9857266.2224 | 779021.5596 | 1834.4 | 3920 | 20 | 1834.4 | 0.00046296 | 0.0352 | 0.00097265 | 0.47598 | 150 | 0.16041 | 0.011547 | 1859.217 | 1859.217 | 1859.2055 | 0.22% | 1833.4 | 1 | 25.8055 | 25.817 |  |  |  |  | Water Kiosk 3 | 40 | 35.2 | 2.4 | PN10