## Survey Data
Station | Northing (m) | Easting (m) | Elevation (m) | Description
0+000.00 | 9869157.075 | 787472.264 | 1873.175 | Borehole
0+020.00 | 9869146.9267 | 787455.0355 | 1873.21 | Spotheight
0+040.00 | 9869135.8551 | 787438.381 | 1873.249 | Spotheight
0+060.00 | 9869124.9273 | 787421.6333 | 1873.356 | Spotheight
0+080.00 | 9869116.1636 | 787403.6666 | 1873.508 | Spotheight
0+100.00 | 9869106.5639 | 787386.1215 | 1873.635 | Spotheight
0+120.00 | 9869096.6369 | 787368.7632 | 1873.688 | Spotheight
0+140.00 | 9869086.3108 | 787351.6381 | 1873.754 | Spotheight
0+160.00 | 9869075.4645 | 787334.8542 | 1873.816 | Spotheight
0+180.00 | 9869064.9601 | 787317.8543 | 1873.865 | Spotheight
0+200.00 | 9869057.8535 | 787299.1809 | 1873.957 | Spotheight
0+220.00 | 9869051.6882 | 787280.1778 | 1873.98 | Spotheight
0+240.00 | 9869044.51 | 787261.5172 | 1873.995 | Spotheight
0+260.00 | 9869036.1064 | 787243.3976 | 1873.996 | Nkairowuani Kiosk 1
0+280.00 | 9869024.2022 | 787227.628 | 1873.997 | Spotheight
0+300.00 | 9869005.5321 | 787220.5775 | 1873.873 | Spotheight
0+320.00 | 9868986.0567 | 787216.0361 | 1873.725 | Spotheight
0+340.00 | 9868966.5553 | 787211.5982 | 1873.568 | Spotheight
0+360.00 | 9868946.9542 | 787207.6792 | 1873.397 | Spotheight
0+380.00 | 9868927.1914 | 787204.6078 | 1873.205 | Spotheight
0+400.00 | 9868907.747 | 787200.0786 | 1873.02 | Spotheight
0+420.00 | 9868888.5179 | 787194.5794 | 1872.841 | Spotheight
0+440.00 | 9868871.4438 | 787184.3609 | 1872.705 | Spotheight
0+460.00 | 9868854.5996 | 787173.6492 | 1872.573 | Spotheight
0+480.00 | 9868835.7443 | 787166.98 | 1872.385 | Spotheight
0+500.00 | 9868816.5621 | 787161.5966 | 1872.226 | Spotheight
0+520.00 | 9868796.775 | 787158.6866 | 1872.067 | Spotheight
0+540.00 | 9868777.8583 | 787153.1486 | 1871.927 | Spotheight
0+560.00 | 9868760.7253 | 787142.8305 | 1871.792 | Spotheight
0+580.00 | 9868742.7192 | 787134.2579 | 1871.663 | Spotheight
0+600.00 | 9868724.154 | 787126.8192 | 1871.516 | Spotheight
0+620.00 | 9868704.7627 | 787122.2944 | 1870.674 | Nkairowuani lagga
0+640.00 | 9868685.0949 | 787118.7909 | 1871.618 | Spotheight
0+660.00 | 9868665.1272 | 787117.6557 | 1871.598 | Spotheight
0+680.00 | 9868645.6318 | 787113.6606 | 1871.616 | Spotheight
0+700.00 | 9868626.4037 | 787108.1577 | 1871.653 | Spotheight
0+720.00 | 9868607.6465 | 787101.2543 | 1871.7 | Spotheight
0+740.00 | 9868588.9344 | 787094.2155 | 1871.749 | Spotheight
0+760.00 | 9868569.7319 | 787088.6242 | 1871.806 | Spotheight
0+780.00 | 9868550.7382 | 787082.4482 | 1871.907 | Spotheight
0+800.00 | 9868532.3948 | 787074.4783 | 1872.147 | Spotheight
0+820.00 | 9868513.5359 | 787068.0393 | 1872.325 | Spotheight
0+840.00 | 9868494.0731 | 787063.4348 | 1872.442 | Spotheight
0+860.00 | 9868474.3044 | 787060.6217 | 1872.6 | Spotheight
0+880.00 | 9868454.4113 | 787058.5565 | 1872.818 | Spotheight
0+900.00 | 9868434.5045 | 787056.6287 | 1872.957 | Spotheight
0+920.00 | 9868414.6117 | 787054.5917 | 1873.117 | Spotheight
0+940.00 | 9868394.8647 | 787051.421 | 1873.392 | Spotheight
0+960.00 | 9868375.0727 | 787048.6679 | 1873.659 | Spotheight
0+980.00 | 9868355.0957 | 787047.7095 | 1873.884 | Spotheight
1+000.00 | 9868335.1365 | 787046.5014 | 1874.113 | Spotheight
1+020.00 | 9868315.2273 | 787044.5972 | 1874.354 | Spotheight
1+040.00 | 9868295.3182 | 787042.6929 | 1874.552 | Spotheight
1+060.00 | 9868275.409 | 787040.7887 | 1874.701 | Spotheight
1+080.00 | 9868255.4999 | 787038.8844 | 1874.908 | Spotheight
1+100.00 | 9868235.588 | 787037.0148 | 1875.164 | Spotheight
1+120.00 | 9868215.6241 | 787035.8139 | 1875.371 | Spotheight
1+140.00 | 9868195.6615 | 787034.5953 | 1875.588 | Spotheight
1+160.00 | 9868175.7504 | 787032.7115 | 1875.835 | Spotheight
1+180.00 | 9868155.8536 | 787030.6967 | 1876.093 | Spotheight
1+200.00 | 9868136.005 | 787028.2409 | 1876.398 | Spotheight
1+220.00 | 9868116.0961 | 787026.3752 | 1876.613 | Spotheight
1+240.00 | 9868096.1599 | 787024.7785 | 1876.833 | Spotheight
1+260.00 | 9868076.2917 | 787022.5113 | 1877.068 | Spotheight
1+280.00 | 9868056.4411 | 787020.0717 | 1877.328 | Spotheight
1+300.00 | 9868036.5354 | 787018.1438 | 1877.547 | Spotheight
1+320.00 | 9868016.6189 | 787016.3189 | 1877.752 | Spotheight
1+340.00 | 9867996.6963 | 787014.5604 | 1877.925 | Spotheight
1+360.00 | 9867976.7717 | 787012.8259 | 1878.105 | Spotheight
1+380.00 | 9867956.8441 | 787011.1255 | 1878.325 | Spotheight
1+400.00 | 9867937.0649 | 787013.5657 | 1878.432 | Spotheight
1+420.00 | 9867917.5156 | 787017.6274 | 1878.519 | Spotheight
1+440.00 | 9867898.3739 | 787023.4233 | 1878.589 | Spotheight
1+460.00 | 9867879.5287 | 787030.0937 | 1878.669 | Spotheight
1+480.00 | 9867860.8159 | 787037.1527 | 1878.753 | Spotheight
1+500.00 | 9867841.5833 | 787042.5974 | 1878.876 | Spotheight
1+520.00 | 9867822.2674 | 787047.7819 | 1879.003 | Spotheight
1+540.00 | 9867803.1678 | 787053.7152 | 1879.077 | Spotheight
1+560.00 | 9867783.9946 | 787059.3291 | 1879.153 | Spotheight
1+580.00 | 9867764.0049 | 787058.7762 | 1879.261 | Spotheight
1+600.00 | 9867744.0207 | 787058.034 | 1879.376 | Spotheight
1+620.00 | 9867724.0762 | 787056.5446 | 1879.523 | Spotheight
1+640.00 | 9867704.2055 | 787054.4662 | 1879.674 | Spotheight
1+660.00 | 9867684.5246 | 787050.9079 | 1879.834 | Spotheight
1+680.00 | 9867664.7584 | 787047.9879 | 1879.991 | Spotheight
1+700.00 | 9867644.829 | 787046.308 | 1880.144 | Spotheight
1+720.00 | 9867624.9451 | 787044.2252 | 1880.287 | Spotheight
1+740.00 | 9867605.1445 | 787041.4079 | 1880.412 | Spotheight
1+760.00 | 9867585.331 | 787038.6945 | 1880.538 | Spotheight
1+780.00 | 9867565.4451 | 787036.561 | 1880.673 | Spotheight
1+800.00 | 9867545.5451 | 787034.6018 | 1880.804 | Spotheight
1+820.00 | 9867525.5723 | 787033.5608 | 1880.92 | Spotheight
1+840.00 | 9867505.6358 | 787032.2253 | 1881.038 | Spotheight
1+860.00 | 9867486.2931 | 787027.1401 | 1881.192 | Spotheight
1+880.00 | 9867467.0189 | 787021.8222 | 1881.345 | Spotheight
1+900.00 | 9867448.0196 | 787015.575 | 1881.495 | Spotheight
1+920.00 | 9867429.3258 | 787008.599 | 1881.641 | Spotheight
1+940.00 | 9867411.6804 | 786999.1843 | 1881.777 | Spotheight
1+960.00 | 9867393.8738 | 786990.0996 | 1881.923 | Spotheight
1+980.00 | 9867375.5743 | 786982.0295 | 1882.1 | Spotheight
2+000.00 | 9867357.1674 | 786974.2147 | 1882.264 | Spotheight
2+020.00 | 9867338.5957 | 786966.7923 | 1882.407 | Spotheight
2+040.00 | 9867320.2293 | 786958.9283 | 1882.556 | Spotheight
2+060.00 | 9867302.6497 | 786949.3911 | 1882.724 | Spotheight
2+080.00 | 9867284.8706 | 786940.2927 | 1882.894 | Spotheight
2+100.00 | 9867266.0061 | 786933.6494 | 1883.071 | Spotheight
2+120.00 | 9867247.0958 | 786927.139 | 1883.232 | Spotheight
2+140.00 | 9867228.1538 | 786920.7202 | 1883.382 | Spotheight
2+160.00 | 9867210.3269 | 786911.7944 | 1883.589 | Spotheight
2+180.00 | 9867192.9048 | 786901.9742 | 1883.813 | Spotheight
2+200.00 | 9867175.0435 | 786892.9758 | 1883.966 | Spotheight
2+220.00 | 9867157.1182 | 786884.1093 | 1884.124 | Spotheight
2+240.00 | 9867138.981 | 786875.6807 | 1884.294 | Spotheight
2+260.00 | 9867121.5562 | 786865.933 | 1884.492 | Spotheight
2+280.00 | 9867104.5898 | 786855.3433 | 1884.708 | Spotheight
2+300.00 | 9867086.7464 | 786846.3118 | 1884.816 | Spotheight
2+320.00 | 9867068.8452 | 786837.3954 | 1884.928 | Spotheight
2+340.00 | 9867050.6954 | 786828.9941 | 1885.077 | Spotheight
2+360.00 | 9867032.5523 | 786820.578 | 1885.246 | Spotheight
2+380.00 | 9867014.4265 | 786812.1251 | 1885.464 | Spotheight
2+400.00 | 9866996.3523 | 786803.5634 | 1885.657 | Spotheight
2+420.00 | 9866978.3618 | 786794.8262 | 1885.81 | Spotheight
2+440.00 | 9866961.0668 | 786784.8318 | 1885.976 | Spotheight
2+460.00 | 9866944.1288 | 786774.1967 | 1886.15 | Spotheight
2+480.00 | 9866927.2381 | 786763.487 | 1886.318 | Spotheight
2+500.00 | 9866910.3713 | 786752.7394 | 1886.482 | Spotheight
2+520.00 | 9866893.9381 | 786741.3445 | 1886.605 | Spotheight
2+540.00 | 9866877.5851 | 786729.8302 | 1886.721 | Spotheight
2+560.00 | 9866862.0463 | 786717.2523 | 1886.882 | Spotheight
2+580.00 | 9866846.6737 | 786704.4584 | 1887.053 | Spotheight
2+600.00 | 9866831.0631 | 786691.9571 | 1887.218 | Spotheight
2+620.00 | 9866815.4096 | 786679.5084 | 1887.383 | Spotheight
2+640.00 | 9866800.1112 | 786666.6274 | 1887.578 | Spotheight
2+660.00 | 9866784.7818 | 786653.7897 | 1887.774 | Spotheight
2+680.00 | 9866767.4951 | 786643.7317 | 1887.916 | Spotheight
2+700.00 | 9866750.2544 | 786633.5956 | 1888.044 | Spotheight
2+720.00 | 9866732.4822 | 786633.2271 | 1888.138 | Spotheight
2+740.00 | 9866718.9436 | 786647.948 | 1888.222 | Spotheight
2+760.00 | 9866706.768 | 786663.8052 | 1888.211 | Spotheight
2+780.00 | 9866694.739 | 786679.7834 | 1888.187 | Spotheight
2+800.00 | 9866682.3763 | 786695.5046 | 1888.156 | Spotheight
2+820.00 | 9866669.9996 | 786711.215 | 1888.125 | Spotheight
2+840.00 | 9866657.5873 | 786726.8973 | 1888.089 | Spotheight
2+860.00 | 9866645.157 | 786742.5653 | 1888.051 | Spotheight
2+880.00 | 9866632.7263 | 786758.2331 | 1888.011 | Spotheight
2+900.00 | 9866620.2937 | 786773.8993 | 1887.959 | Spotheight
2+920.00 | 9866607.8611 | 786789.5655 | 1887.907 | Spotheight
2+940.00 | 9866595.4638 | 786805.2597 | 1887.859 | Spotheight
2+960.00 | 9866583.0719 | 786820.9581 | 1887.811 | Spotheight
2+980.00 | 9866570.7853 | 786836.7387 | 1887.763 | Spotheight
3+000.00 | 9866558.5673 | 786852.5729 | 1887.716 | Spotheight
3+020.00 | 9866546.3317 | 786868.3934 | 1887.672 | Spotheight
3+040.00 | 9866534.0891 | 786884.2086 | 1887.631 | Spotheight
3+060.00 | 9866521.8199 | 786900.003 | 1887.589 | Spotheight
3+080.00 | 9866509.511 | 786915.7667 | 1887.547 | Spotheight
3+100.00 | 9866497.2059 | 786931.5332 | 1887.494 | Spotheight
3+120.00 | 9866484.9063 | 786947.3041 | 1887.421 | Spotheight
3+140.00 | 9866472.5721 | 786963.0478 | 1887.354 | Spotheight
3+160.00 | 9866460.2062 | 786978.7668 | 1887.29 | Spotheight
3+180.00 | 9866447.7293 | 786994.3974 | 1887.196 | Spotheight
3+200.00 | 9866435.2081 | 787009.9929 | 1887.091 | Spotheight
3+220.00 | 9866422.7976 | 787025.676 | 1886.984 | Spotheight
3+240.00 | 9866410.5022 | 787041.4502 | 1886.875 | Spotheight
3+260.00 | 9866398.0637 | 787057.1107 | 1886.765 | Spotheight
3+280.00 | 9866385.4896 | 787072.6635 | 1886.653 | Spotheight
3+300.00 | 9866373.1246 | 787088.3819 | 1886.519 | Spotheight
3+320.00 | 9866360.8792 | 787104.1949 | 1886.373 | Spotheight
3+340.00 | 9866348.5533 | 787119.9451 | 1886.237 | Spotheight
3+360.00 | 9866336.2101 | 787135.6819 | 1886.103 | Spotheight
3+380.00 | 9866323.8036 | 787151.3687 | 1885.965 | Spotheight
3+400.00 | 9866311.3814 | 787167.0432 | 1885.825 | Spotheight
3+420.00 | 9866299.0309 | 787182.774 | 1885.692 | Spotheight
3+440.00 | 9866286.7418 | 787198.553 | 1885.565 | Spotheight
3+460.00 | 9866274.2937 | 787214.2044 | 1885.431 | Spotheight
3+480.00 | 9866261.5326 | 787229.6041 | 1885.285 | Spotheight
3+500.00 | 9866247.8599 | 787244.1296 | 1885.156 | Spotheight
3+520.00 | 9866232.9471 | 787257.4566 | 1885.049 | Spotheight
3+540.00 | 9866215.957 | 787267.8011 | 1884.949 | Spotheight
3+560.00 | 9866198.2204 | 787277.043 | 1884.853 | Spotheight
3+580.00 | 9866179.9396 | 787285.1354 | 1884.775 | Spotheight
3+600.00 | 9866161.545 | 787292.9866 | 1884.701 | Spotheight
3+620.00 | 9866143.2519 | 787301.0708 | 1884.599 | Spotheight
3+640.00 | 9866124.9637 | 787309.1663 | 1884.494 | Spotheight
3+660.00 | 9866106.5345 | 787316.9356 | 1884.413 | Spotheight
3+680.00 | 9866088.2155 | 787324.9545 | 1884.329 | Spotheight
3+700.00 | 9866070.0665 | 787333.3576 | 1884.241 | Spotheight
3+720.00 | 9866051.8717 | 787341.6608 | 1884.162 | Spotheight
3+740.00 | 9866033.6517 | 787349.909 | 1884.055 | Spotheight
3+760.00 | 9866015.2999 | 787357.857 | 1883.987 | Spotheight
3+780.00 | 9865996.8987 | 787365.6924 | 1883.932 | Spotheight
3+800.00 | 9865978.4507 | 787373.4172 | 1883.838 | Spotheight
3+820.00 | 9865960.0007 | 787381.137 | 1883.741 | Spotheight
3+840.00 | 9865941.5758 | 787388.9166 | 1883.645 | Spotheight
3+860.00 | 9865923.1619 | 787396.7223 | 1883.549 | Spotheight
3+880.00 | 9865904.8333 | 787404.7242 | 1883.461 | Spotheight
3+900.00 | 9865886.565 | 787412.8648 | 1883.379 | Spotheight
3+920.00 | 9865868.6928 | 787421.767 | 1883.299 | Spotheight
3+940.00 | 9865851.5768 | 787432.1131 | 1883.224 | Spotheight
3+960.00 | 9865836.41 | 787444.8937 | 1883.123 | Spotheight
3+980.00 | 9865822.7297 | 787459.4832 | 1883.004 | Spotheight
4+000.00 | 9865808.5105 | 787473.54 | 1882.902 | Spotheight
4+020.00 | 9865794.0812 | 787487.389 | 1882.808 | Spotheight
4+040.00 | 9865779.5745 | 787501.1568 | 1882.695 | Spotheight
4+060.00 | 9865765.101 | 787514.9562 | 1882.578 | Spotheight
4+080.00 | 9865751.7685 | 787529.864 | 1882.463 | Spotheight
4+100.00 | 9865738.1967 | 787544.5385 | 1882.349 | Spotheight
4+120.00 | 9865723.5751 | 787558.1843 | 1882.237 | Spotheight
4+140.00 | 9865709.146 | 787572.0292 | 1882.122 | Spotheight
4+160.00 | 9865695.0236 | 787586.1911 | 1882.002 | Spotheight
4+180.00 | 9865680.9283 | 787600.3799 | 1881.894 | Spotheight
4+200.00 | 9865666.8615 | 787614.5969 | 1881.798 | Spotheight
4+220.00 | 9865652.5787 | 787628.5939 | 1881.681 | Spotheight
4+240.00 | 9865638.099 | 787642.3902 | 1881.546 | Spotheight
4+260.00 | 9865623.8519 | 787656.4238 | 1881.429 | Spotheight
4+280.00 | 9865609.7725 | 787670.6284 | 1881.323 | Spotheight
4+300.00 | 9865595.6099 | 787684.7485 | 1881.217 | Spotheight
4+320.00 | 9865581.1949 | 787698.6124 | 1881.108 | Spotheight
4+340.00 | 9865566.829 | 787712.5267 | 1880.998 | Spotheight
4+360.00 | 9865552.6077 | 787726.5892 | 1880.885 | Spotheight
4+380.00 | 9865538.3864 | 787740.6518 | 1880.778 | Spotheight
4+400.00 | 9865524.1652 | 787754.7143 | 1880.68 | Spotheight
4+420.00 | 9865509.7958 | 787768.6239 | 1880.592 | Spotheight
4+440.00 | 9865495.2795 | 787782.3817 | 1880.516 | Spotheight
4+460.00 | 9865480.9259 | 787796.3085 | 1880.448 | Spotheight
4+480.00 | 9865466.6257 | 787810.2907 | 1880.381 | Spotheight
4+500.00 | 9865452.2389 | 787824.1839 | 1880.32 | Spotheight
4+520.00 | 9865437.8323 | 787838.0565 | 1880.26 | Spotheight
4+540.00 | 9865423.3475 | 787851.8471 | 1880.221 | Spotheight
4+560.00 | 9865408.8115 | 787865.5841 | 1880.196 | Spotheight
4+580.00 | 9865394.405 | 787879.4545 | 1880.159 | Spotheight
4+600.00 | 9865380.2453 | 787893.579 | 1880.102 | Spotheight
4+620.00 | 9865365.8463 | 787907.4563 | 1880.067 | Spotheight
4+640.00 | 9865351.2658 | 787921.146 | 1880.049 | Spotheight
4+660.00 | 9865336.9408 | 787935.1021 | 1880.006 | Spotheight
4+680.00 | 9865322.6598 | 787949.104 | 1879.96 | Spotheight
4+700.00 | 9865307.8236 | 787962.5158 | 1879.925 | Spotheight
4+720.00 | 9865292.9776 | 787975.9171 | 1879.889 | Spotheight
4+740.00 | 9865278.5997 | 787989.8193 | 1879.9 | Spotheight
4+760.00 | 9865264.2386 | 788003.7387 | 1879.902 | Spotheight
4+780.00 | 9865250.1537 | 788017.9379 | 1879.692 | Spotheight
4+800.00 | 9865236.0689 | 788032.1371 | 1879.482 | Spotheight
4+820.00 | 9865222.018 | 788046.3699 | 1879.322 | Spotheight
4+832.87 | 9865212.989 | 788055.536 | 1879.234 | Nkairowuani Kiosk 2

## Water Demand
Item | Units
B.H Yield | 9.5 | m³/Hr
Population Targeted | 2000 | people
Water demand per capita | 20 | L/d/p
Total Water Demand per day | 40000 | Litres
Reservoir capacity required (tank) | 40 | m³
Reservoir | 100 | m³
Unmet Demand | -60 | m³
Note:
20 litres per capita per day should be assured to take care of basic hygiene needs and basic food hygiene (WHO)
Assumption: | 1 day | 8 hrs | Pump operational for10 hrs

## Pump Design
BOREHOLE DATA
BH depth (m) = |  |  | 184
Pump level present (m) = |  |  | 175
Yield (m3/hr) = |  |  | 9.5 | 6.3333 | 66.67%
Head
Pump level |  |  |  |  | 175
Frictional Losses |  |  |  |  | 28.7519
delivery head |  |  |  |  | 14.403
Tank height |  |  |  |  | 1
Residual head |  |  | 15% |  | 6.6232
|  | Total Head |  |  | 225.7781
POWER REQUIREMENT
H (m) | Q (L/Sec) | Constant |  |  | Pump efficiency |  | KW
225.7781 | 1.7593 | 102 |  |  | 0.65 |  | 5.991
add factor genset safety |  |  |  |  | 1.5 | 8.9865 | KW
[6 empty] | 11.2331 | KVA

## Rising Main - Tank & WK 2
NKAIRUWANI WATER PROJECT
Contract No.: | [17 empty] | Soil Cover | 1 |  | Assumption: | Discharge | 0.0017593
Profile levels - end of line included
Date: 21.09.2022 | [27 empty] | Pipe Details
Nodes | Station | Northing(m) | Easting(m) | Elevation(m) | Chainage | Length (m) | Orig. Ground Level | Discharge (m3/s) | Internal diameter (m) | Area (m2) | Velocity (m/s) | C | HL | Vf | El Static | EL | HGL | Slope (%) | Pipe invert (m) | Depth of excavation (m) | Hp | Hs | Off-take (m3/s) | Total flow (m3/s) | Bends | Losses due to bends | Remarks | External Diameter (mm) | Internal Diameter (mm) | Wall Thickness (mm) | Class | Soil Type
| 0+000 | 9869157.075 | 787472.264 | 1873.175 | 0 | 0 | 1873.175 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0 | 0.027176 | 1922.9531 | 1922.9531 | 1922.9259 |  | 1872.175 | 1 | 50.7509 | 50.7781 |  | 0.0017593 |  |  | Top Borehole Casing Cover START | 63 | 55.4 | 3.8 | PN 10.0
| 0+020 | 9869146.9267 | 787455.0355 | 1873.21 | 20 | 20 | 1873.21 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1922.7444 | 1922.7172 | 0.175% | 1872.21 | 1 | 50.5072 | 50.7431 |  |  |  |  | Ground Level Pumphouse Perimeter Fence | 63 | 55.4 | 3.8 | PN 10.0
| 0+040 | 9869135.8551 | 787438.381 | 1873.249 | 40 | 20 | 1873.249 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1922.5357 | 1922.5085 | 0.195% | 1872.249 | 1 | 50.2595 | 50.7041 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+060 | 9869124.9273 | 787421.6333 | 1873.356 | 60 | 20 | 1873.356 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1922.327 | 1922.2998 | 0.535% | 1872.356 | 1 | 49.9438 | 50.5971 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+080 | 9869116.1636 | 787403.6666 | 1873.508 | 80 | 20 | 1873.508 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1922.1182 | 1922.0911 | 0.76% | 1872.508 | 1 | 49.5831 | 50.4451 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+100 | 9869106.5639 | 787386.1215 | 1873.635 | 100 | 20 | 1873.635 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1921.9095 | 1921.8823 | 0.635% | 1872.635 | 1 | 49.2473 | 50.3181 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+120 | 9869096.6369 | 787368.7632 | 1873.688 | 120 | 20 | 1873.688 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1921.7008 | 1921.6736 | 0.265% | 1872.688 | 1 | 48.9856 | 50.2651 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+140 | 9869086.3108 | 787351.6381 | 1873.754 | 140 | 20 | 1873.754 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1921.4921 | 1921.4649 | 0.33% | 1872.754 | 1 | 48.7109 | 50.1991 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+160 | 9869075.4645 | 787334.8542 | 1873.816 | 160 | 20 | 1873.816 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1921.2833 | 1921.2562 | 0.31% | 1872.816 | 1 | 48.4402 | 50.1371 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+180 | 9869064.9601 | 787317.8543 | 1873.865 | 180 | 20 | 1873.865 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1921.0746 | 1921.0474 | 0.245% | 1872.865 | 1 | 48.1824 | 50.0881 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+200 | 9869057.8535 | 787299.1809 | 1873.957 | 200 | 20 | 1873.957 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1920.8659 | 1920.8387 | 0.46% | 1872.957 | 1 | 47.8817 | 49.9961 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+220 | 9869051.6882 | 787280.1778 | 1873.98 | 220 | 20 | 1873.98 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1920.6572 | 1920.63 | 0.115% | 1872.98 | 1 | 47.65 | 49.9731 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+240 | 9869044.51 | 787261.5172 | 1873.995 | 240 | 20 | 1873.995 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1920.4484 | 1920.4213 | 0.075% | 1872.995 | 1 | 47.4263 | 49.9581 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+260 | 9869036.1064 | 787243.3976 | 1873.996 | 260 | 20 | 1873.996 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1920.2397 | 1920.2125 | 0.005% | 1872.996 | 1 | 47.2165 | 49.9571 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+280 | 9869024.2022 | 787227.628 | 1873.997 | 280 | 20 | 1873.997 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1920.031 | 1920.0038 | 0.005% | 1872.997 | 1 | 47.0068 | 49.9561 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+300 | 9869005.5321 | 787220.5775 | 1873.873 | 300 | 20 | 1873.873 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1919.8223 | 1919.7951 | -0.62% | 1872.873 | 1 | 46.9221 | 50.0801 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+320 | 9868986.0567 | 787216.0361 | 1873.725 | 320 | 20 | 1873.725 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1919.6135 | 1919.5864 | -0.74% | 1872.725 | 1 | 46.8614 | 50.2281 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+340 | 9868966.5553 | 787211.5982 | 1873.568 | 340 | 20 | 1873.568 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1919.4048 | 1919.3776 | -0.785% | 1872.568 | 1 | 46.8096 | 50.3851 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+360 | 9868946.9542 | 787207.6792 | 1873.397 | 360 | 20 | 1873.397 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1919.1961 | 1919.1689 | -0.855% | 1872.397 | 1 | 46.7719 | 50.5561 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+380 | 9868927.1914 | 787204.6078 | 1873.205 | 380 | 20 | 1873.205 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1918.9874 | 1918.9602 | -0.96% | 1872.205 | 1 | 46.7552 | 50.7481 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+400 | 9868907.747 | 787200.0786 | 1873.02 | 400 | 20 | 1873.02 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1918.7787 | 1918.7515 | -0.925% | 1872.02 | 1 | 46.7315 | 50.9331 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+420 | 9868888.5179 | 787194.5794 | 1872.841 | 420 | 20 | 1872.841 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1918.5699 | 1918.5428 | -0.895% | 1871.841 | 1 | 46.7018 | 51.1121 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+440 | 9868871.4438 | 787184.3609 | 1872.705 | 440 | 20 | 1872.705 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1918.3612 | 1918.334 | -0.68% | 1871.705 | 1 | 46.629 | 51.2481 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+460 | 9868854.5996 | 787173.6492 | 1872.573 | 460 | 20 | 1872.573 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1918.1525 | 1918.1253 | -0.66% | 1871.573 | 1 | 46.5523 | 51.3801 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+480 | 9868835.7443 | 787166.98 | 1872.385 | 480 | 20 | 1872.385 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1917.9438 | 1917.9166 | -0.94% | 1871.385 | 1 | 46.5316 | 51.5681 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+500 | 9868816.5621 | 787161.5966 | 1872.226 | 500 | 20 | 1872.226 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1917.735 | 1917.7079 | -0.795% | 1871.226 | 1 | 46.4819 | 51.7271 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+520 | 9868796.775 | 787158.6866 | 1872.067 | 520 | 20 | 1872.067 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1917.5263 | 1917.4991 | -0.795% | 1871.067 | 1 | 46.4321 | 51.8861 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+540 | 9868777.8583 | 787153.1486 | 1871.927 | 540 | 20 | 1871.927 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1917.3176 | 1917.2904 | -0.7% | 1870.927 | 1 | 46.3634 | 52.0261 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+560 | 9868760.7253 | 787142.8305 | 1871.792 | 560 | 20 | 1871.792 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1917.1089 | 1917.0817 | -0.675% | 1870.792 | 1 | 46.2897 | 52.1611 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+580 | 9868742.7192 | 787134.2579 | 1871.663 | 580 | 20 | 1871.663 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1916.9001 | 1916.873 | -0.645% | 1870.663 | 1 | 46.21 | 52.2901 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+600 | 9868724.154 | 787126.8192 | 1871.516 | 600 | 20 | 1871.516 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1916.6914 | 1916.6642 | -1.38% | 1870.516 | 1 | 46.1482 | 52.4371 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+620 | 9868704.7627 | 787122.2944 | 1870.674 | 620 | 20 | 1870.674 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1916.4827 | 1916.4555 | -4.945% | 1869.674 | 1 | 46.7815 | 53.2791 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+640 | 9868685.0949 | 787118.7909 | 1871.618 | 640 | 20 | 1871.618 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1916.274 | 1916.2468 | 0.51% | 1870.618 | 1 | 45.6288 | 52.3351 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+660 | 9868665.1272 | 787117.6557 | 1871.598 | 660 | 20 | 1871.598 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1916.0652 | 1916.0381 | 4.62% | 1870.598 | 1 | 45.4401 | 52.3551 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+680 | 9868645.6318 | 787113.6606 | 1871.616 | 680 | 20 | 1871.616 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1915.8565 | 1915.8293 | -0.01% | 1870.616 | 1 | 45.2133 | 52.3371 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+700 | 9868626.4037 | 787108.1577 | 1871.653 | 700 | 20 | 1871.653 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1915.6478 | 1915.6206 | 0.275% | 1870.653 | 1 | 44.9676 | 52.3001 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+720 | 9868607.6465 | 787101.2543 | 1871.7 | 720 | 20 | 1871.7 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1915.4391 | 1915.4119 | 0.42% | 1870.7 | 1 | 44.7119 | 52.2531 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+740 | 9868588.9344 | 787094.2155 | 1871.749 | 740 | 20 | 1871.749 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1915.2303 | 1915.2032 | 0.48% | 1870.749 | 1 | 44.4542 | 52.2041 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+760 | 9868569.7319 | 787088.6242 | 1871.806 | 760 | 20 | 1871.806 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1915.0216 | 1914.9944 | 0.53% | 1870.806 | 1 | 44.1884 | 52.1471 |  |  |  |  | ARV D75 (Double Orifice) | 63 | 55.4 | 3.8 | PN 10.0
| 0+780 | 9868550.7382 | 787082.4482 | 1871.907 | 780 | 20 | 1871.907 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1914.8129 | 1914.7857 | 0.79% | 1870.907 | 1 | 43.8787 | 52.0461 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+800 | 9868532.3948 | 787074.4783 | 1872.147 | 800 | 20 | 1872.147 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1914.6042 | 1914.577 | 1.705% | 1871.147 | 1 | 43.43 | 51.8061 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+820 | 9868513.5359 | 787068.0393 | 1872.325 | 820 | 20 | 1872.325 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1914.3955 | 1914.3683 | 2.09% | 1871.325 | 1 | 43.0433 | 51.6281 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+840 | 9868494.0731 | 787063.4348 | 1872.442 | 840 | 20 | 1872.442 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1914.1867 | 1914.1596 | 1.475% | 1871.442 | 1 | 42.7176 | 51.5111 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+860 | 9868474.3044 | 787060.6217 | 1872.6 | 860 | 20 | 1872.6 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1913.978 | 1913.9508 | 1.375% | 1871.6 | 1 | 42.3508 | 51.3531 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+880 | 9868454.4113 | 787058.5565 | 1872.818 | 880 | 20 | 1872.818 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1913.7693 | 1913.7421 | 1.88% | 1871.818 | 1 | 41.9241 | 51.1351 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+900 | 9868434.5045 | 787056.6287 | 1872.957 | 900 | 20 | 1872.957 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1913.5606 | 1913.5334 | 1.785% | 1871.957 | 1 | 41.5764 | 50.9961 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+920 | 9868414.6117 | 787054.5917 | 1873.117 | 920 | 20 | 1873.117 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1913.3518 | 1913.3247 | 1.495% | 1872.117 | 1 | 41.2077 | 50.8361 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+940 | 9868394.8647 | 787051.421 | 1873.392 | 940 | 20 | 1873.392 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1913.1431 | 1913.1159 | 2.175% | 1872.392 | 1 | 40.7239 | 50.5611 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+960 | 9868375.0727 | 787048.6679 | 1873.659 | 960 | 20 | 1873.659 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1912.9344 | 1912.9072 | 2.71% | 1872.659 | 1 | 40.2482 | 50.2941 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 0+980 | 9868355.0957 | 787047.7095 | 1873.884 | 980 | 20 | 1873.884 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1912.7257 | 1912.6985 | 2.46% | 1872.884 | 1 | 39.8145 | 50.0691 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+000 | 9868335.1365 | 787046.5014 | 1874.113 | 1000 | 20 | 1874.113 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1912.5169 | 1912.4898 | 2.27% | 1873.113 | 1 | 39.3768 | 49.8401 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+020 | 9868315.2273 | 787044.5972 | 1874.354 | 1020 | 20 | 1874.354 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1912.3082 | 1912.281 | 2.35% | 1873.354 | 1 | 38.927 | 49.5991 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+040 | 9868295.3182 | 787042.6929 | 1874.552 | 1040 | 20 | 1874.552 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1912.0995 | 1912.0723 | 2.195% | 1873.552 | 1 | 38.5203 | 49.4011 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+060 | 9868275.409 | 787040.7887 | 1874.701 | 1060 | 20 | 1874.701 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1911.8908 | 1911.8636 | 1.735% | 1873.701 | 1 | 38.1626 | 49.2521 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+080 | 9868255.4999 | 787038.8844 | 1874.908 | 1080 | 20 | 1874.908 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1911.682 | 1911.6549 | 1.78% | 1873.908 | 1 | 37.7469 | 49.0451 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+100 | 9868235.588 | 787037.0148 | 1875.164 | 1100 | 20 | 1875.164 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1911.4733 | 1911.4461 | 2.315% | 1874.164 | 1 | 37.2821 | 48.7891 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+120 | 9868215.6241 | 787035.8139 | 1875.371 | 1120 | 20 | 1875.371 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1911.2646 | 1911.2374 | 2.315% | 1874.371 | 1 | 36.8664 | 48.5821 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+140 | 9868195.6615 | 787034.5953 | 1875.588 | 1140 | 20 | 1875.588 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1911.0559 | 1911.0287 | 2.12% | 1874.588 | 1 | 36.4407 | 48.3651 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+160 | 9868175.7504 | 787032.7115 | 1875.835 | 1160 | 20 | 1875.835 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1910.8472 | 1910.82 | 2.32% | 1874.835 | 1 | 35.985 | 48.1181 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+180 | 9868155.8536 | 787030.6967 | 1876.093 | 1180 | 20 | 1876.093 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1910.6384 | 1910.6113 | 2.525% | 1875.093 | 1 | 35.5183 | 47.8601 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+200 | 9868136.005 | 787028.2409 | 1876.398 | 1200 | 20 | 1876.398 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1910.4297 | 1910.4025 | 2.815% | 1875.398 | 1 | 35.0045 | 47.5551 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+220 | 9868116.0961 | 787026.3752 | 1876.613 | 1220 | 20 | 1876.613 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1910.221 | 1910.1938 | 2.6% | 1875.613 | 1 | 34.5808 | 47.3401 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+240 | 9868096.1599 | 787024.7785 | 1876.833 | 1240 | 20 | 1876.833 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1910.0123 | 1909.9851 | 2.175% | 1875.833 | 1 | 34.1521 | 47.1201 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+260 | 9868076.2917 | 787022.5113 | 1877.068 | 1260 | 20 | 1877.068 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1909.8035 | 1909.7764 | 2.275% | 1876.068 | 1 | 33.7084 | 46.8851 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+280 | 9868056.4411 | 787020.0717 | 1877.328 | 1280 | 20 | 1877.328 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1909.5948 | 1909.5676 | 2.475% | 1876.328 | 1 | 33.2396 | 46.6251 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+300 | 9868036.5354 | 787018.1438 | 1877.547 | 1300 | 20 | 1877.547 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1909.3861 | 1909.3589 | 2.395% | 1876.547 | 1 | 32.8119 | 46.4061 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+320 | 9868016.6189 | 787016.3189 | 1877.752 | 1320 | 20 | 1877.752 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1909.1774 | 1909.1502 | 2.12% | 1876.752 | 1 | 32.3982 | 46.2011 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+340 | 9867996.6963 | 787014.5604 | 1877.925 | 1340 | 20 | 1877.925 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1908.9686 | 1908.9415 | 1.89% | 1876.925 | 1 | 32.0165 | 46.0281 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+360 | 9867976.7717 | 787012.8259 | 1878.105 | 1360 | 20 | 1878.105 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1908.7599 | 1908.7327 | 1.765% | 1877.105 | 1 | 31.6277 | 45.8481 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+380 | 9867956.8441 | 787011.1255 | 1878.325 | 1380 | 20 | 1878.325 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1908.5512 | 1908.524 | 2% | 1877.325 | 1 | 31.199 | 45.6281 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+400 | 9867937.0649 | 787013.5657 | 1878.432 | 1400 | 20 | 1878.432 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1908.3425 | 1908.3153 | 1.635% | 1877.432 | 1 | 30.8833 | 45.5211 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+420 | 9867917.5156 | 787017.6274 | 1878.519 | 1420 | 20 | 1878.519 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1908.1337 | 1908.1066 | 0.97% | 1877.519 | 1 | 30.5876 | 45.4341 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+440 | 9867898.3739 | 787023.4233 | 1878.589 | 1440 | 20 | 1878.589 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1907.925 | 1907.8978 | 0.785% | 1877.589 | 1 | 30.3088 | 45.3641 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+460 | 9867879.5287 | 787030.0937 | 1878.669 | 1460 | 20 | 1878.669 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1907.7163 | 1907.6891 | 0.75% | 1877.669 | 1 | 30.0201 | 45.2841 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+480 | 9867860.8159 | 787037.1527 | 1878.753 | 1480 | 20 | 1878.753 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1907.5076 | 1907.4804 | 0.82% | 1877.753 | 1 | 29.7274 | 45.2001 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+500 | 9867841.5833 | 787042.5974 | 1878.876 | 1500 | 20 | 1878.876 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1907.2988 | 1907.2717 | 1.035% | 1877.876 | 1 | 29.3957 | 45.0771 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+520 | 9867822.2674 | 787047.7819 | 1879.003 | 1520 | 20 | 1879.003 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1907.0901 | 1907.0629 | 1.25% | 1878.003 | 1 | 29.0599 | 44.9501 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+540 | 9867803.1678 | 787053.7152 | 1879.077 | 1540 | 20 | 1879.077 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1906.8814 | 1906.8542 | 1.005% | 1878.077 | 1 | 28.7772 | 44.8761 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+560 | 9867783.9946 | 787059.3291 | 1879.153 | 1560 | 20 | 1879.153 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1906.6727 | 1906.6455 | 0.75% | 1878.153 | 1 | 28.4925 | 44.8001 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+580 | 9867764.0049 | 787058.7762 | 1879.261 | 1580 | 20 | 1879.261 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1906.464 | 1906.4368 | 0.92% | 1878.261 | 1 | 28.1758 | 44.6921 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+600 | 9867744.0207 | 787058.034 | 1879.376 | 1600 | 20 | 1879.376 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1906.2552 | 1906.2281 | 1.115% | 1878.376 | 1 | 27.8521 | 44.5771 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+620 | 9867724.0762 | 787056.5446 | 1879.523 | 1620 | 20 | 1879.523 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1906.0465 | 1906.0193 | 1.31% | 1878.523 | 1 | 27.4963 | 44.4301 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+640 | 9867704.2055 | 787054.4662 | 1879.674 | 1640 | 20 | 1879.674 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1905.8378 | 1905.8106 | 1.49% | 1878.674 | 1 | 27.1366 | 44.2791 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+660 | 9867684.5246 | 787050.9079 | 1879.834 | 1660 | 20 | 1879.834 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1905.6291 | 1905.6019 | 1.555% | 1878.834 | 1 | 26.7679 | 44.1191 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+680 | 9867664.7584 | 787047.9879 | 1879.991 | 1680 | 20 | 1879.991 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1905.4203 | 1905.3932 | 1.585% | 1878.991 | 1 | 26.4022 | 43.9621 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+700 | 9867644.829 | 787046.308 | 1880.144 | 1700 | 20 | 1880.144 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1905.2116 | 1905.1844 | 1.55% | 1879.144 | 1 | 26.0404 | 43.8091 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+720 | 9867624.9451 | 787044.2252 | 1880.287 | 1720 | 20 | 1880.287 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1905.0029 | 1904.9757 | 1.48% | 1879.287 | 1 | 25.6887 | 43.6661 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+740 | 9867605.1445 | 787041.4079 | 1880.412 | 1740 | 20 | 1880.412 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1904.7942 | 1904.767 | 1.34% | 1879.412 | 1 | 25.355 | 43.5411 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+760 | 9867585.331 | 787038.6945 | 1880.538 | 1760 | 20 | 1880.538 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1904.5854 | 1904.5583 | 1.255% | 1879.538 | 1 | 25.0203 | 43.4151 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+780 | 9867565.4451 | 787036.561 | 1880.673 | 1780 | 20 | 1880.673 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1904.3767 | 1904.3495 | 1.305% | 1879.673 | 1 | 24.6765 | 43.2801 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+800 | 9867545.5451 | 787034.6018 | 1880.804 | 1800 | 20 | 1880.804 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1904.168 | 1904.1408 | 1.33% | 1879.804 | 1 | 24.3368 | 43.1491 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+820 | 9867525.5723 | 787033.5608 | 1880.92 | 1820 | 20 | 1880.92 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1903.9593 | 1903.9321 | 1.235% | 1879.92 | 1 | 24.0121 | 43.0331 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+840 | 9867505.6358 | 787032.2253 | 1881.038 | 1840 | 20 | 1881.038 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1903.7505 | 1903.7234 | 1.17% | 1880.038 | 1 | 23.6854 | 42.9151 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+860 | 9867486.2931 | 787027.1401 | 1881.192 | 1860 | 20 | 1881.192 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1903.5418 | 1903.5146 | 1.36% | 1880.192 | 1 | 23.3226 | 42.7611 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+880 | 9867467.0189 | 787021.8222 | 1881.345 | 1880 | 20 | 1881.345 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1903.3331 | 1903.3059 | 1.535% | 1880.345 | 1 | 22.9609 | 42.6081 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+900 | 9867448.0196 | 787015.575 | 1881.495 | 1900 | 20 | 1881.495 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1903.1244 | 1903.0972 | 1.515% | 1880.495 | 1 | 22.6022 | 42.4581 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+920 | 9867429.3258 | 787008.599 | 1881.641 | 1920 | 20 | 1881.641 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1902.9157 | 1902.8885 | 1.48% | 1880.641 | 1 | 22.2475 | 42.3121 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+940 | 9867411.6804 | 786999.1843 | 1881.777 | 1940 | 20 | 1881.777 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1902.7069 | 1902.6798 | 1.41% | 1880.777 | 1 | 21.9028 | 42.1761 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+960 | 9867393.8738 | 786990.0996 | 1881.923 | 1960 | 20 | 1881.923 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1902.4982 | 1902.471 | 1.41% | 1880.923 | 1 | 21.548 | 42.0301 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 1+980 | 9867375.5743 | 786982.0295 | 1882.1 | 1980 | 20 | 1882.1 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1902.2895 | 1902.2623 | 1.615% | 1881.1 | 1 | 21.1623 | 41.8531 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+000 | 9867357.1674 | 786974.2147 | 1882.264 | 2000 | 20 | 1882.264 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1902.0808 | 1902.0536 | 1.705% | 1881.264 | 1 | 20.7896 | 41.6891 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+020 | 9867338.5957 | 786966.7923 | 1882.407 | 2020 | 20 | 1882.407 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1901.872 | 1901.8449 | 1.535% | 1881.407 | 1 | 20.4379 | 41.5461 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+040 | 9867320.2293 | 786958.9283 | 1882.556 | 2040 | 20 | 1882.556 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1901.6633 | 1901.6361 | 1.46% | 1881.556 | 1 | 20.0801 | 41.3971 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+060 | 9867302.6497 | 786949.3911 | 1882.724 | 2060 | 20 | 1882.724 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1901.4546 | 1901.4274 | 1.585% | 1881.724 | 1 | 19.7034 | 41.2291 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+080 | 9867284.8706 | 786940.2927 | 1882.894 | 2080 | 20 | 1882.894 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1901.2459 | 1901.2187 | 1.69% | 1881.894 | 1 | 19.3247 | 41.0591 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
ARV D56 | 2+100 | 9867266.0061 | 786933.6494 | 1883.071 | 2100 | 20 | 1883.071 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1901.0371 | 1901.01 | 1.735% | 1882.071 | 1 | 18.939 | 40.8821 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+120 | 9867247.0958 | 786927.139 | 1883.232 | 2120 | 20 | 1883.232 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1900.8284 | 1900.8012 | 1.69% | 1882.232 | 1 | 18.5692 | 40.7211 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+140 | 9867228.1538 | 786920.7202 | 1883.382 | 2140 | 20 | 1883.382 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1900.6197 | 1900.5925 | 1.555% | 1882.382 | 1 | 18.2105 | 40.5711 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+160 | 9867210.3269 | 786911.7944 | 1883.589 | 2160 | 20 | 1883.589 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1900.411 | 1900.3838 | 1.785% | 1882.589 | 1 | 17.7948 | 40.3641 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+180 | 9867192.9048 | 786901.9742 | 1883.813 | 2180 | 20 | 1883.813 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1900.2022 | 1900.1751 | 2.155% | 1882.813 | 1 | 17.3621 | 40.1401 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+200 | 9867175.0435 | 786892.9758 | 1883.966 | 2200 | 20 | 1883.966 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1899.9935 | 1899.9663 | 1.885% | 1882.966 | 1 | 17.0003 | 39.9871 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+220 | 9867157.1182 | 786884.1093 | 1884.124 | 2220 | 20 | 1884.124 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1899.7848 | 1899.7576 | 1.555% | 1883.124 | 1 | 16.6336 | 39.8291 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+240 | 9867138.981 | 786875.6807 | 1884.294 | 2240 | 20 | 1884.294 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1899.5761 | 1899.5489 | 1.64% | 1883.294 | 1 | 16.2549 | 39.6591 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+260 | 9867121.5562 | 786865.933 | 1884.492 | 2260 | 20 | 1884.492 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1899.3673 | 1899.3402 | 1.84% | 1883.492 | 1 | 15.8482 | 39.4611 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+280 | 9867104.5898 | 786855.3433 | 1884.708 | 2280 | 20 | 1884.708 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1899.1586 | 1899.1314 | 2.07% | 1883.708 | 1 | 15.4234 | 39.2451 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+300 | 9867086.7464 | 786846.3118 | 1884.816 | 2300 | 20 | 1884.816 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1898.9499 | 1898.9227 | 1.62% | 1883.816 | 1 | 15.1067 | 39.1371 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+320 | 9867068.8452 | 786837.3954 | 1884.928 | 2320 | 20 | 1884.928 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1898.7412 | 1898.714 | 1.1% | 1883.928 | 1 | 14.786 | 39.0251 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+340 | 9867050.6954 | 786828.9941 | 1885.077 | 2340 | 20 | 1885.077 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1898.5325 | 1898.5053 | 1.305% | 1884.077 | 1 | 14.4283 | 38.8761 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+360 | 9867032.5523 | 786820.578 | 1885.246 | 2360 | 20 | 1885.246 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1898.3237 | 1898.2966 | 1.59% | 1884.246 | 1 | 14.0506 | 38.7071 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+380 | 9867014.4265 | 786812.1251 | 1885.464 | 2380 | 20 | 1885.464 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1898.115 | 1898.0878 | 1.935% | 1884.464 | 1 | 13.6238 | 38.4891 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+400 | 9866996.3523 | 786803.5634 | 1885.657 | 2400 | 20 | 1885.657 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1897.9063 | 1897.8791 | 2.055% | 1884.657 | 1 | 13.2221 | 38.2961 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+420 | 9866978.3618 | 786794.8262 | 1885.81 | 2420 | 20 | 1885.81 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1897.6976 | 1897.6704 | 1.73% | 1884.81 | 1 | 12.8604 | 38.1431 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+440 | 9866961.0668 | 786784.8318 | 1885.976 | 2440 | 20 | 1885.976 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1897.4888 | 1897.4617 | 1.595% | 1884.976 | 1 | 12.4857 | 37.9771 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+460 | 9866944.1288 | 786774.1967 | 1886.15 | 2460 | 20 | 1886.15 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1897.2801 | 1897.2529 | 1.7% | 1885.15 | 1 | 12.1029 | 37.8031 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+480 | 9866927.2381 | 786763.487 | 1886.318 | 2480 | 20 | 1886.318 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1897.0714 | 1897.0442 | 1.71% | 1885.318 | 1 | 11.7262 | 37.6351 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+500 | 9866910.3713 | 786752.7394 | 1886.482 | 2500 | 20 | 1886.482 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1896.8627 | 1896.8355 | 1.66% | 1885.482 | 1 | 11.3535 | 37.4711 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+520 | 9866893.9381 | 786741.3445 | 1886.605 | 2520 | 20 | 1886.605 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1896.6539 | 1896.6268 | 1.435% | 1885.605 | 1 | 11.0218 | 37.3481 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+540 | 9866877.5851 | 786729.8302 | 1886.721 | 2540 | 20 | 1886.721 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1896.4452 | 1896.418 | 1.195% | 1885.721 | 1 | 10.697 | 37.2321 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+560 | 9866862.0463 | 786717.2523 | 1886.882 | 2560 | 20 | 1886.882 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1896.2365 | 1896.2093 | 1.385% | 1885.882 | 1 | 10.3273 | 37.0711 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+580 | 9866846.6737 | 786704.4584 | 1887.053 | 2580 | 20 | 1887.053 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1896.0278 | 1896.0006 | 1.66% | 1886.053 | 1 | 9.9476 | 36.9001 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+600 | 9866831.0631 | 786691.9571 | 1887.218 | 2600 | 20 | 1887.218 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1895.819 | 1895.7919 | 1.68% | 1886.218 | 1 | 9.5739 | 36.7351 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+620 | 9866815.4096 | 786679.5084 | 1887.383 | 2620 | 20 | 1887.383 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1895.6103 | 1895.5831 | 1.65% | 1886.383 | 1 | 9.2001 | 36.5701 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+640 | 9866800.1112 | 786666.6274 | 1887.578 | 2640 | 20 | 1887.578 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 150 | 0.20872 | 0.027176 | 1922.9531 | 1895.4016 | 1895.3744 | 1.8% | 1886.578 | 1 | 8.7964 | 36.3751 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+660 | 9866784.7818 | 786653.7897 | 1887.774 | 2660 | 20 | 1887.774 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 151 | 0.20617 | 0.027176 | 1922.9531 | 1895.1954 | 1895.1683 | 1.955% | 1886.774 | 1 | 8.3943 | 36.1791 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+680 | 9866767.4951 | 786643.7317 | 1887.916 | 2680 | 20 | 1887.916 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 152 | 0.20367 | 0.027176 | 1922.9531 | 1894.9918 | 1894.9646 | 1.69% | 1886.916 | 1 | 8.0486 | 36.0371 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+700 | 9866750.2544 | 786633.5956 | 1888.044 | 2700 | 20 | 1888.044 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 153 | 0.20121 | 0.027176 | 1922.9531 | 1894.7906 | 1894.7634 | 1.35% | 1887.044 | 1 | 7.7194 | 35.9091 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+720 | 9866732.4822 | 786633.2271 | 1888.138 | 2720 | 20 | 1888.138 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 154 | 0.19879 | 0.027176 | 1922.9531 | 1894.5918 | 1894.5646 | 1.11% | 1887.138 | 1 | 7.4266 | 35.8151 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+740 | 9866718.9436 | 786647.948 | 1888.222 | 2740 | 20 | 1888.222 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 155 | 0.19643 | 0.027176 | 1922.9531 | 1894.3953 | 1894.3682 | 0.89% | 1887.222 | 1 | 7.1462 | 35.7311 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
| 2+760 | 9866706.768 | 786663.8052 | 1888.211 | 2760 | 20 | 1888.211 | 0.0017593 | 0.0554 | 0.0024093 | 0.7302 | 156 | 0.1941 | 0.027176 | 1922.9531 | 1894.2012 | 1894.1741 | 0.365% | 1887.211 | 1 | 6.9631 | 35.7421 | [5 empty] | 63 | 55.4 | 3.8 | PN 10.0
28.7519

## Dist - Tank to WK 3
NKAIRUWANI WATER SUPPLY PROJECT
Contract No.: | [17 empty] | Soil Cover | 1 |  | Assumption: | Discharge | 0.00087963
Profile levels - end of line included
Date: 21.09.2022 | [27 empty] | Pipe Details
Nodes | Station | Northing(m) | Easting(m) | Elevation(m) | Chainage | Length (m) | Orig. Ground Level | Discharge (m3/s) | Internal diameter (m) | Area (m2) | Velocity (m/s) | C | HL | Vf | El Static | EL | HGL | Slope (%) | Pipe invert (m) | Depth of excavation (m) | Hp | Hs | Off-take (m3/s) | Total flow (m3/s) | Bends | Losses due to bends | Remarks | External Diameter (mm) | Internal Diameter (mm) | Wall Thickness (mm) | Class | Soil Type
| 0+000 | 9866694.739 | 786679.7834 | 1888.187 | 0 | 0 | 1888.187 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 |  | 1887.187 | 1 | 0.95831 | 1 |  | 0.00087963 |  |  |  | 40 | 35.2 | 2.4 | PN 10
| 0+020 | 9866682.3763 | 786695.5046 | 1888.156 | 20 | 20 | 1888.156 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.155% | 1887.156 | 1 | 0.98931 | 1.031 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+040 | 9866669.9996 | 786711.215 | 1888.125 | 40 | 20 | 1888.125 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.155% | 1887.125 | 1 | 1.0203 | 1.062 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+060 | 9866657.5873 | 786726.8973 | 1888.089 | 60 | 20 | 1888.089 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.18% | 1887.089 | 1 | 1.0563 | 1.098 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+080 | 9866645.157 | 786742.5653 | 1888.051 | 80 | 20 | 1888.051 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.19% | 1887.051 | 1 | 1.0943 | 1.136 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+100 | 9866632.7263 | 786758.2331 | 1888.011 | 100 | 20 | 1888.011 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.2% | 1887.011 | 1 | 1.1343 | 1.176 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+120 | 9866620.2937 | 786773.8993 | 1887.959 | 120 | 20 | 1887.959 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.26% | 1886.959 | 1 | 1.1863 | 1.228 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+140 | 9866607.8611 | 786789.5655 | 1887.907 | 140 | 20 | 1887.907 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.26% | 1886.907 | 1 | 1.2383 | 1.28 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+160 | 9866595.4638 | 786805.2597 | 1887.859 | 160 | 20 | 1887.859 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.24% | 1886.859 | 1 | 1.2863 | 1.328 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+180 | 9866583.0719 | 786820.9581 | 1887.811 | 180 | 20 | 1887.811 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.24% | 1886.811 | 1 | 1.3343 | 1.376 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+200 | 9866570.7853 | 786836.7387 | 1887.763 | 200 | 20 | 1887.763 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.24% | 1886.763 | 1 | 1.3823 | 1.424 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+220 | 9866558.5673 | 786852.5729 | 1887.716 | 220 | 20 | 1887.716 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.235% | 1886.716 | 1 | 1.4293 | 1.471 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+240 | 9866546.3317 | 786868.3934 | 1887.672 | 240 | 20 | 1887.672 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.22% | 1886.672 | 1 | 1.4733 | 1.515 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+260 | 9866534.0891 | 786884.2086 | 1887.631 | 260 | 20 | 1887.631 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.205% | 1886.631 | 1 | 1.5143 | 1.556 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+280 | 9866521.8199 | 786900.003 | 1887.589 | 280 | 20 | 1887.589 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.21% | 1886.589 | 1 | 1.5563 | 1.598 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+300 | 9866509.511 | 786915.7667 | 1887.547 | 300 | 20 | 1887.547 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.21% | 1886.547 | 1 | 1.5983 | 1.64 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+320 | 9866497.2059 | 786931.5332 | 1887.494 | 320 | 20 | 1887.494 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.265% | 1886.494 | 1 | 1.6513 | 1.693 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+340 | 9866484.9063 | 786947.3041 | 1887.421 | 340 | 20 | 1887.421 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.365% | 1886.421 | 1 | 1.7243 | 1.766 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+360 | 9866472.5721 | 786963.0478 | 1887.354 | 360 | 20 | 1887.354 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.335% | 1886.354 | 1 | 1.7913 | 1.833 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+380 | 9866460.2062 | 786978.7668 | 1887.29 | 380 | 20 | 1887.29 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.32% | 1886.29 | 1 | 1.8553 | 1.897 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+400 | 9866447.7293 | 786994.3974 | 1887.196 | 400 | 20 | 1887.196 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.47% | 1886.196 | 1 | 1.9493 | 1.991 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+420 | 9866435.2081 | 787009.9929 | 1887.091 | 420 | 20 | 1887.091 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.525% | 1886.091 | 1 | 2.0543 | 2.096 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+440 | 9866422.7976 | 787025.676 | 1886.984 | 440 | 20 | 1886.984 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.535% | 1885.984 | 1 | 2.1613 | 2.203 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+460 | 9866410.5022 | 787041.4502 | 1886.875 | 460 | 20 | 1886.875 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.545% | 1885.875 | 1 | 2.2703 | 2.312 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+480 | 9866398.0637 | 787057.1107 | 1886.765 | 480 | 20 | 1886.765 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.55% | 1885.765 | 1 | 2.3803 | 2.422 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+500 | 9866385.4896 | 787072.6635 | 1886.653 | 500 | 20 | 1886.653 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.56% | 1885.653 | 1 | 2.4923 | 2.534 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+520 | 9866373.1246 | 787088.3819 | 1886.519 | 520 | 20 | 1886.519 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.67% | 1885.519 | 1 | 2.6263 | 2.668 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+540 | 9866360.8792 | 787104.1949 | 1886.373 | 540 | 20 | 1886.373 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.73% | 1885.373 | 1 | 2.7723 | 2.814 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+560 | 9866348.5533 | 787119.9451 | 1886.237 | 560 | 20 | 1886.237 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.68% | 1885.237 | 1 | 2.9083 | 2.95 | 0 |  |  |  |  | 40 | 35.2 | 2.4 | PN 10
| 0+580 | 9866336.2101 | 787135.6819 | 1886.103 | 580 | 20 | 1886.103 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.67% | 1885.103 | 1 | 3.0423 | 3.084 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+600 | 9866323.8036 | 787151.3687 | 1885.965 | 600 | 20 | 1885.965 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.69% | 1884.965 | 1 | 3.1803 | 3.222 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+620 | 9866311.3814 | 787167.0432 | 1885.825 | 620 | 20 | 1885.825 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.7% | 1884.825 | 1 | 3.3203 | 3.362 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+640 | 9866299.0309 | 787182.774 | 1885.692 | 640 | 20 | 1885.692 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.665% | 1884.692 | 1 | 3.4533 | 3.495 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+660 | 9866286.7418 | 787198.553 | 1885.565 | 660 | 20 | 1885.565 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.635% | 1884.565 | 1 | 3.5803 | 3.622 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+680 | 9866274.2937 | 787214.2044 | 1885.431 | 680 | 20 | 1885.431 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.67% | 1884.431 | 1 | 3.7143 | 3.756 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+700 | 9866261.5326 | 787229.6041 | 1885.285 | 700 | 20 | 1885.285 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.73% | 1884.285 | 1 | 3.8603 | 3.902 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+720 | 9866247.8599 | 787244.1296 | 1885.156 | 720 | 20 | 1885.156 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.645% | 1884.156 | 1 | 3.9893 | 4.031 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+740 | 9866232.9471 | 787257.4566 | 1885.049 | 740 | 20 | 1885.049 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.535% | 1884.049 | 1 | 4.0963 | 4.138 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+760 | 9866215.957 | 787267.8011 | 1884.949 | 760 | 20 | 1884.949 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.5% | 1883.949 | 1 | 4.1963 | 4.238 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+780 | 9866198.2204 | 787277.043 | 1884.853 | 780 | 20 | 1884.853 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.48% | 1883.853 | 1 | 4.2923 | 4.334 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+800 | 9866179.9396 | 787285.1354 | 1884.775 | 800 | 20 | 1884.775 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.39% | 1883.775 | 1 | 4.3703 | 4.412 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+820 | 9866161.545 | 787292.9866 | 1884.701 | 820 | 20 | 1884.701 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.37% | 1883.701 | 1 | 4.4443 | 4.486 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+840 | 9866143.2519 | 787301.0708 | 1884.599 | 840 | 20 | 1884.599 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.51% | 1883.599 | 1 | 4.5463 | 4.588 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+860 | 9866124.9637 | 787309.1663 | 1884.494 | 860 | 20 | 1884.494 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.525% | 1883.494 | 1 | 4.6513 | 4.693 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+880 | 9866106.5345 | 787316.9356 | 1884.413 | 880 | 20 | 1884.413 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.405% | 1883.413 | 1 | 4.7323 | 4.774 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+900 | 9866088.2155 | 787324.9545 | 1884.329 | 900 | 20 | 1884.329 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.42% | 1883.329 | 1 | 4.8163 | 4.858 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+920 | 9866070.0665 | 787333.3576 | 1884.241 | 920 | 20 | 1884.241 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.44% | 1883.241 | 1 | 4.9043 | 4.946 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+940 | 9866051.8717 | 787341.6608 | 1884.162 | 940 | 20 | 1884.162 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.395% | 1883.162 | 1 | 4.9833 | 5.025 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+960 | 9866033.6517 | 787349.909 | 1884.055 | 960 | 20 | 1884.055 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.535% | 1883.055 | 1 | 5.0903 | 5.132 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+980 | 9866015.2999 | 787357.857 | 1883.987 | 980 | 20 | 1883.987 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.34% | 1882.987 | 1 | 5.1583 | 5.2 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+1000 | 9865996.8987 | 787365.6924 | 1883.932 | 1000 | 20 | 1883.932 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.275% | 1882.932 | 1 | 5.2133 | 5.255 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+1020 | 9865978.4507 | 787373.4172 | 1883.838 | 1020 | 20 | 1883.838 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.47% | 1882.838 | 1 | 5.3073 | 5.349 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1040 | 9865960.0007 | 787381.137 | 1883.741 | 1040 | 20 | 1883.741 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.485% | 1882.741 | 1 | 5.4043 | 5.446 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1060 | 9865941.5758 | 787388.9166 | 1883.645 | 1060 | 20 | 1883.645 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.48% | 1882.645 | 1 | 5.5003 | 5.542 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1080 | 9865923.1619 | 787396.7223 | 1883.549 | 1080 | 20 | 1883.549 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.48% | 1882.549 | 1 | 5.5963 | 5.638 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1100 | 9865904.8333 | 787404.7242 | 1883.461 | 1100 | 20 | 1883.461 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.44% | 1882.461 | 1 | 5.6843 | 5.726 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1120 | 9865886.565 | 787412.8648 | 1883.379 | 1120 | 20 | 1883.379 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.41% | 1882.379 | 1 | 5.7663 | 5.808 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1140 | 9865868.6928 | 787421.767 | 1883.299 | 1140 | 20 | 1883.299 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.4% | 1882.299 | 1 | 5.8463 | 5.888 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1160 | 9865851.5768 | 787432.1131 | 1883.224 | 1160 | 20 | 1883.224 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.375% | 1882.224 | 1 | 5.9213 | 5.963 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1180 | 9865836.41 | 787444.8937 | 1883.123 | 1180 | 20 | 1883.123 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.505% | 1882.123 | 1 | 6.0223 | 6.064 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1200 | 9865822.7297 | 787459.4832 | 1883.004 | 1200 | 20 | 1883.004 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.595% | 1882.004 | 1 | 6.1413 | 6.183 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1220 | 9865808.5105 | 787473.54 | 1882.902 | 1220 | 20 | 1882.902 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.51% | 1881.902 | 1 | 6.2433 | 6.285 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1240 | 9865794.0812 | 787487.389 | 1882.808 | 1240 | 20 | 1882.808 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.47% | 1881.808 | 1 | 6.3373 | 6.379 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1260 | 9865779.5745 | 787501.1568 | 1882.695 | 1260 | 20 | 1882.695 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.565% | 1881.695 | 1 | 6.4503 | 6.492 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1280 | 9865765.101 | 787514.9562 | 1882.578 | 1280 | 20 | 1882.578 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.585% | 1881.578 | 1 | 6.5673 | 6.609 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1300 | 9865751.7685 | 787529.864 | 1882.463 | 1300 | 20 | 1882.463 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.575% | 1881.463 | 1 | 6.6823 | 6.724 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1320 | 9865738.1967 | 787544.5385 | 1882.349 | 1320 | 20 | 1882.349 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.57% | 1881.349 | 1 | 6.7963 | 6.838 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1340 | 9865723.5751 | 787558.1843 | 1882.237 | 1340 | 20 | 1882.237 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.56% | 1881.237 | 1 | 6.9083 | 6.95 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1360 | 9865709.146 | 787572.0292 | 1882.122 | 1360 | 20 | 1882.122 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.575% | 1881.122 | 1 | 7.0233 | 7.065 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1380 | 9865695.0236 | 787586.1911 | 1882.002 | 1380 | 20 | 1882.002 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.6% | 1881.002 | 1 | 7.1433 | 7.185 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1400 | 9865680.9283 | 787600.3799 | 1881.894 | 1400 | 20 | 1881.894 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.54% | 1880.894 | 1 | 7.2513 | 7.293 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1420 | 9865666.8615 | 787614.5969 | 1881.798 | 1420 | 20 | 1881.798 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.48% | 1880.798 | 1 | 7.3473 | 7.389 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1440 | 9865652.5787 | 787628.5939 | 1881.681 | 1440 | 20 | 1881.681 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.585% | 1880.681 | 1 | 7.4643 | 7.506 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1460 | 9865638.099 | 787642.3902 | 1881.546 | 1460 | 20 | 1881.546 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.675% | 1880.546 | 1 | 7.5993 | 7.641 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1480 | 9865623.8519 | 787656.4238 | 1881.429 | 1480 | 20 | 1881.429 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.585% | 1880.429 | 1 | 7.7163 | 7.758 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1500 | 9865609.7725 | 787670.6284 | 1881.323 | 1500 | 20 | 1881.323 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.53% | 1880.323 | 1 | 7.8223 | 7.864 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1520 | 9865595.6099 | 787684.7485 | 1881.217 | 1520 | 20 | 1881.217 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.53% | 1880.217 | 1 | 7.9283 | 7.97 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1540 | 9865581.1949 | 787698.6124 | 1881.108 | 1540 | 20 | 1881.108 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.545% | 1880.108 | 1 | 8.0373 | 8.079 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1560 | 9865566.829 | 787712.5267 | 1880.998 | 1560 | 20 | 1880.998 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.55% | 1879.998 | 1 | 8.1473 | 8.189 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1580 | 9865552.6077 | 787726.5892 | 1880.885 | 1580 | 20 | 1880.885 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.565% | 1879.885 | 1 | 8.2603 | 8.302 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1600 | 9865538.3864 | 787740.6518 | 1880.778 | 1600 | 20 | 1880.778 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.535% | 1879.778 | 1 | 8.3673 | 8.409 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1620 | 9865524.1652 | 787754.7143 | 1880.68 | 1620 | 20 | 1880.68 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.49% | 1879.68 | 1 | 8.4653 | 8.507 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1640 | 9865509.7958 | 787768.6239 | 1880.592 | 1640 | 20 | 1880.592 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.44% | 1879.592 | 1 | 8.5533 | 8.595 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1660 | 9865495.2795 | 787782.3817 | 1880.516 | 1660 | 20 | 1880.516 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.38% | 1879.516 | 1 | 8.6293 | 8.671 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1680 | 9865480.9259 | 787796.3085 | 1880.448 | 1680 | 20 | 1880.448 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.34% | 1879.448 | 1 | 8.6973 | 8.739 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1700 | 9865466.6257 | 787810.2907 | 1880.381 | 1700 | 20 | 1880.381 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.335% | 1879.381 | 1 | 8.7643 | 8.806 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1720 | 9865452.2389 | 787824.1839 | 1880.32 | 1720 | 20 | 1880.32 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.305% | 1879.32 | 1 | 8.8253 | 8.867 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1740 | 9865437.8323 | 787838.0565 | 1880.26 | 1740 | 20 | 1880.26 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.3% | 1879.26 | 1 | 8.8853 | 8.927 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1760 | 9865423.3475 | 787851.8471 | 1880.221 | 1760 | 20 | 1880.221 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.195% | 1879.221 | 1 | 8.9243 | 8.966 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1780 | 9865408.8115 | 787865.5841 | 1880.196 | 1780 | 20 | 1880.196 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.125% | 1879.196 | 1 | 8.9493 | 8.991 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1800 | 9865394.405 | 787879.4545 | 1880.159 | 1800 | 20 | 1880.159 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.185% | 1879.159 | 1 | 8.9863 | 9.028 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1820 | 9865380.2453 | 787893.579 | 1880.102 | 1820 | 20 | 1880.102 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.285% | 1879.102 | 1 | 9.0433 | 9.085 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1840 | 9865365.8463 | 787907.4563 | 1880.067 | 1840 | 20 | 1880.067 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.175% | 1879.067 | 1 | 9.0783 | 9.12 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1860 | 9865351.2658 | 787921.146 | 1880.049 | 1860 | 20 | 1880.049 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.09% | 1879.049 | 1 | 9.0963 | 9.138 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1880 | 9865336.9408 | 787935.1021 | 1880.006 | 1880 | 20 | 1880.006 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.215% | 1879.006 | 1 | 9.1393 | 9.181 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1900 | 9865322.6598 | 787949.104 | 1879.96 | 1900 | 20 | 1879.96 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.23% | 1878.96 | 1 | 9.1853 | 9.227 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1920 | 9865307.8236 | 787962.5158 | 1879.925 | 1920 | 20 | 1879.925 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.175% | 1878.925 | 1 | 9.2203 | 9.262 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1940 | 9865292.9776 | 787975.9171 | 1879.889 | 1940 | 20 | 1879.889 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.18% | 1878.889 | 1 | 9.2563 | 9.298 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1960 | 9865278.5997 | 787989.8193 | 1879.9 | 1960 | 20 | 1879.9 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.055% | 1878.9 | 1 | 9.2453 | 9.287 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+1980 | 9865264.2386 | 788003.7387 | 1879.902 | 1980 | 20 | 1879.902 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.01% | 1878.902 | 1 | 9.2433 | 9.285 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+2000 | 9865250.1537 | 788017.9379 | 1879.692 | 2000 | 20 | 1879.692 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -1.05% | 1878.692 | 1 | 9.4533 | 9.495 | [5 empty] | 40 | 35.2 | 2.4 | PN 8
| 0+2020 | 9865236.0689 | 788032.1371 | 1879.482 | 2020 | 20 | 1879.482 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -1.05% | 1878.482 | 1 | 9.6633 | 9.705 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+2040 | 9865222.018 | 788046.3699 | 1879.322 | 2040 | 20 | 1879.322 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.8% | 1878.322 | 1 | 9.8233 | 9.865 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+2060 | 9865212.989 | 788055.536 | 1879.234 | 2060 | 20 | 1879.234 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.44% | 1878.234 | 1 | 9.9113 | 9.953 | [5 empty] | 40 | 35.2 | 2.4 | PN 10

## Return - Tank to WK 1
NKAIRUWANI WATER SUPPLY PROJECT
Contract No.: | [17 empty] | Soil Cover | 1 |  | Assumption: | Discharge | 0.00087963
Profile levels - end of line included
Date: 21.09.2022 | [27 empty] | Pipe Details
Nodes | Station | Northing(m) | Easting(m) | Elevation(m) | Chainage | Length (m) | Orig. Ground Level | Discharge (m3/s) | Internal diameter (m) | Area (m2) | Velocity (m/s) | C | HL | Vf | El Static | EL | HGL | Slope (%) | Pipe invert (m) | Depth of excavation (m) | Hp | Hs | Off-take (m3/s) | Total flow (m3/s) | Bends | Losses due to bends | Remarks | External Diameter (mm) | Internal Diameter (mm) | Wall Thickness (mm) | Class | Soil Type
| 0+000.00 | 9865212.989 | 788055.536 | 1879.234 | 0 | 0 | 1888.187 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 |  | 1887.187 | 1 | 0.95831 | 1 |  | 0.00087963 |  |  |  | 40 | 35.2 | 2.4 | PN 10
| 0+020.00 | 9865222.018 | 788046.3699 | 1879.322 | 20 | 20 | 1888.156 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.44% | 1887.156 | 1 | 0.98931 | 1.031 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+040.00 | 9865236.0689 | 788032.1371 | 1879.482 | 40 | 20 | 1888.125 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.8% | 1887.125 | 1 | 1.0203 | 1.062 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+060.00 | 9865250.1537 | 788017.9379 | 1879.692 | 60 | 20 | 1888.089 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 1.05% | 1887.089 | 1 | 1.0563 | 1.098 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+080.00 | 9865264.2386 | 788003.7387 | 1879.902 | 80 | 20 | 1888.051 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 1.05% | 1887.051 | 1 | 1.0943 | 1.136 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+100.00 | 9865278.5997 | 787989.8193 | 1879.9 | 100 | 20 | 1888.011 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.01% | 1887.011 | 1 | 1.1343 | 1.176 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+120.00 | 9865292.9776 | 787975.9171 | 1879.889 | 120 | 20 | 1887.959 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.055% | 1886.959 | 1 | 1.1863 | 1.228 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+140.00 | 9865307.8236 | 787962.5158 | 1879.925 | 140 | 20 | 1887.907 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.18% | 1886.907 | 1 | 1.2383 | 1.28 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+160.00 | 9865322.6598 | 787949.104 | 1879.96 | 160 | 20 | 1887.859 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.175% | 1886.859 | 1 | 1.2863 | 1.328 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+180.00 | 9865336.9408 | 787935.1021 | 1880.006 | 180 | 20 | 1887.811 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.23% | 1886.811 | 1 | 1.3343 | 1.376 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+200.00 | 9865351.2658 | 787921.146 | 1880.049 | 200 | 20 | 1887.763 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.215% | 1886.763 | 1 | 1.3823 | 1.424 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+220.00 | 9865365.8463 | 787907.4563 | 1880.067 | 220 | 20 | 1887.716 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.09% | 1886.716 | 1 | 1.4293 | 1.471 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+240.00 | 9865380.2453 | 787893.579 | 1880.102 | 240 | 20 | 1887.672 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.175% | 1886.672 | 1 | 1.4733 | 1.515 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+260.00 | 9865394.405 | 787879.4545 | 1880.159 | 260 | 20 | 1887.631 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.285% | 1886.631 | 1 | 1.5143 | 1.556 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+280.00 | 9865408.8115 | 787865.5841 | 1880.196 | 280 | 20 | 1887.589 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.185% | 1886.589 | 1 | 1.5563 | 1.598 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+300.00 | 9865423.3475 | 787851.8471 | 1880.221 | 300 | 20 | 1887.547 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.125% | 1886.547 | 1 | 1.5983 | 1.64 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+320.00 | 9865437.8323 | 787838.0565 | 1880.26 | 320 | 20 | 1887.494 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.195% | 1886.494 | 1 | 1.6513 | 1.693 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+340.00 | 9865452.2389 | 787824.1839 | 1880.32 | 340 | 20 | 1887.421 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.3% | 1886.421 | 1 | 1.7243 | 1.766 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+360.00 | 9865466.6257 | 787810.2907 | 1880.381 | 360 | 20 | 1887.354 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.305% | 1886.354 | 1 | 1.7913 | 1.833 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+380.00 | 9865480.9259 | 787796.3085 | 1880.448 | 380 | 20 | 1887.29 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.335% | 1886.29 | 1 | 1.8553 | 1.897 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+400.00 | 9865495.2795 | 787782.3817 | 1880.516 | 400 | 20 | 1887.196 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.34% | 1886.196 | 1 | 1.9493 | 1.991 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+420.00 | 9865509.7958 | 787768.6239 | 1880.592 | 420 | 20 | 1887.091 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.38% | 1886.091 | 1 | 2.0543 | 2.096 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+440.00 | 9865524.1652 | 787754.7143 | 1880.68 | 440 | 20 | 1886.984 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.44% | 1885.984 | 1 | 2.1613 | 2.203 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+460.00 | 9865538.3864 | 787740.6518 | 1880.778 | 460 | 20 | 1886.875 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.49% | 1885.875 | 1 | 2.2703 | 2.312 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+480.00 | 9865552.6077 | 787726.5892 | 1880.885 | 480 | 20 | 1886.765 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.535% | 1885.765 | 1 | 2.3803 | 2.422 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+500.00 | 9865566.829 | 787712.5267 | 1880.998 | 500 | 20 | 1886.653 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.565% | 1885.653 | 1 | 2.4923 | 2.534 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+520.00 | 9865581.1949 | 787698.6124 | 1881.108 | 520 | 20 | 1886.519 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.55% | 1885.519 | 1 | 2.6263 | 2.668 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+540.00 | 9865595.6099 | 787684.7485 | 1881.217 | 540 | 20 | 1886.373 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.545% | 1885.373 | 1 | 2.7723 | 2.814 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+560.00 | 9865609.7725 | 787670.6284 | 1881.323 | 560 | 20 | 1886.237 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.53% | 1885.237 | 1 | 2.9083 | 2.95 | 0 |  |  |  |  | 40 | 35.2 | 2.4 | PN 10
| 0+580.00 | 9865623.8519 | 787656.4238 | 1881.429 | 580 | 20 | 1886.103 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.53% | 1885.103 | 1 | 3.0423 | 3.084 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+600.00 | 9865638.099 | 787642.3902 | 1881.546 | 600 | 20 | 1885.965 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.585% | 1884.965 | 1 | 3.1803 | 3.222 | [5 empty] | 40 | 35.2 | 2.4 | PN 10 |  | 22.5
| 0+620.00 | 9865652.5787 | 787628.5939 | 1881.681 | 620 | 20 | 1885.825 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.675% | 1884.825 | 1 | 3.3203 | 3.362 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+640.00 | 9865666.8615 | 787614.5969 | 1881.798 | 640 | 20 | 1885.692 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.585% | 1884.692 | 1 | 3.4533 | 3.495 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+660.00 | 9865680.9283 | 787600.3799 | 1881.894 | 660 | 20 | 1885.565 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.48% | 1884.565 | 1 | 3.5803 | 3.622 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+680.00 | 9865695.0236 | 787586.1911 | 1882.002 | 680 | 20 | 1885.431 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.54% | 1884.431 | 1 | 3.7143 | 3.756 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+700.00 | 9865709.146 | 787572.0292 | 1882.122 | 700 | 20 | 1885.285 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.6% | 1884.285 | 1 | 3.8603 | 3.902 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+720.00 | 9865723.5751 | 787558.1843 | 1882.237 | 720 | 20 | 1885.156 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.575% | 1884.156 | 1 | 3.9893 | 4.031 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+740.00 | 9865738.1967 | 787544.5385 | 1882.349 | 740 | 20 | 1885.049 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.56% | 1884.049 | 1 | 4.0963 | 4.138 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+760.00 | 9865751.7685 | 787529.864 | 1882.463 | 760 | 20 | 1884.949 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.57% | 1883.949 | 1 | 4.1963 | 4.238 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+780.00 | 9865765.101 | 787514.9562 | 1882.578 | 780 | 20 | 1884.853 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.575% | 1883.853 | 1 | 4.2923 | 4.334 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+800.00 | 9865779.5745 | 787501.1568 | 1882.695 | 800 | 20 | 1884.775 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.585% | 1883.775 | 1 | 4.3703 | 4.412 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+820.00 | 9865794.0812 | 787487.389 | 1882.808 | 820 | 20 | 1884.701 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.565% | 1883.701 | 1 | 4.4443 | 4.486 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+840.00 | 9865808.5105 | 787473.54 | 1882.902 | 840 | 20 | 1884.599 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.47% | 1883.599 | 1 | 4.5463 | 4.588 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+860.00 | 9865822.7297 | 787459.4832 | 1883.004 | 860 | 20 | 1884.494 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.51% | 1883.494 | 1 | 4.6513 | 4.693 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+880.00 | 9865836.41 | 787444.8937 | 1883.123 | 880 | 20 | 1884.413 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.595% | 1883.413 | 1 | 4.7323 | 4.774 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+900.00 | 9865851.5768 | 787432.1131 | 1883.224 | 900 | 20 | 1884.329 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.505% | 1883.329 | 1 | 4.8163 | 4.858 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+920.00 | 9865868.6928 | 787421.767 | 1883.299 | 920 | 20 | 1884.241 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.375% | 1883.241 | 1 | 4.9043 | 4.946 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+940.00 | 9865886.565 | 787412.8648 | 1883.379 | 940 | 20 | 1884.162 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.4% | 1883.162 | 1 | 4.9833 | 5.025 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+960.00 | 9865904.8333 | 787404.7242 | 1883.461 | 960 | 20 | 1884.055 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.41% | 1883.055 | 1 | 5.0903 | 5.132 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 0+980.00 | 9865923.1619 | 787396.7223 | 1883.549 | 980 | 20 | 1883.987 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.44% | 1882.987 | 1 | 5.1583 | 5.2 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+000.00 | 9865941.5758 | 787388.9166 | 1883.645 | 1000 | 20 | 1883.932 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.48% | 1882.932 | 1 | 5.2133 | 5.255 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+020.00 | 9865960.0007 | 787381.137 | 1883.741 | 1020 | 20 | 1883.838 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.48% | 1882.838 | 1 | 5.3073 | 5.349 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+040.00 | 9865978.4507 | 787373.4172 | 1883.838 | 1040 | 20 | 1883.741 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.485% | 1882.741 | 1 | 5.4043 | 5.446 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+060.00 | 9865996.8987 | 787365.6924 | 1883.932 | 1060 | 20 | 1883.645 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.47% | 1882.645 | 1 | 5.5003 | 5.542 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+080.00 | 9866015.2999 | 787357.857 | 1883.987 | 1080 | 20 | 1883.549 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.275% | 1882.549 | 1 | 5.5963 | 5.638 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+100.00 | 9866033.6517 | 787349.909 | 1884.055 | 1100 | 20 | 1883.461 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.34% | 1882.461 | 1 | 5.6843 | 5.726 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+120.00 | 9866051.8717 | 787341.6608 | 1884.162 | 1120 | 20 | 1883.379 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.535% | 1882.379 | 1 | 5.7663 | 5.808 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+140.00 | 9866070.0665 | 787333.3576 | 1884.241 | 1140 | 20 | 1883.299 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.395% | 1882.299 | 1 | 5.8463 | 5.888 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+160.00 | 9866088.2155 | 787324.9545 | 1884.329 | 1160 | 20 | 1883.224 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.44% | 1882.224 | 1 | 5.9213 | 5.963 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+180.00 | 9866106.5345 | 787316.9356 | 1884.413 | 1180 | 20 | 1883.123 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.42% | 1882.123 | 1 | 6.0223 | 6.064 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+200.00 | 9866124.9637 | 787309.1663 | 1884.494 | 1200 | 20 | 1883.004 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.405% | 1882.004 | 1 | 6.1413 | 6.183 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+220.00 | 9866143.2519 | 787301.0708 | 1884.599 | 1220 | 20 | 1882.902 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.525% | 1881.902 | 1 | 6.2433 | 6.285 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+240.00 | 9866161.545 | 787292.9866 | 1884.701 | 1240 | 20 | 1882.808 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.51% | 1881.808 | 1 | 6.3373 | 6.379 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+260.00 | 9866179.9396 | 787285.1354 | 1884.775 | 1260 | 20 | 1882.695 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.37% | 1881.695 | 1 | 6.4503 | 6.492 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+280.00 | 9866198.2204 | 787277.043 | 1884.853 | 1280 | 20 | 1882.578 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.39% | 1881.578 | 1 | 6.5673 | 6.609 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+300.00 | 9866215.957 | 787267.8011 | 1884.949 | 1300 | 20 | 1882.463 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.48% | 1881.463 | 1 | 6.6823 | 6.724 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+320.00 | 9866232.9471 | 787257.4566 | 1885.049 | 1320 | 20 | 1882.349 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.5% | 1881.349 | 1 | 6.7963 | 6.838 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+340.00 | 9866247.8599 | 787244.1296 | 1885.156 | 1340 | 20 | 1882.237 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.535% | 1881.237 | 1 | 6.9083 | 6.95 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+360.00 | 9866261.5326 | 787229.6041 | 1885.285 | 1360 | 20 | 1882.122 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.645% | 1881.122 | 1 | 7.0233 | 7.065 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+380.00 | 9866274.2937 | 787214.2044 | 1885.431 | 1380 | 20 | 1882.002 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.73% | 1881.002 | 1 | 7.1433 | 7.185 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+400.00 | 9866286.7418 | 787198.553 | 1885.565 | 1400 | 20 | 1881.894 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.67% | 1880.894 | 1 | 7.2513 | 7.293 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+420.00 | 9866299.0309 | 787182.774 | 1885.692 | 1420 | 20 | 1881.798 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.635% | 1880.798 | 1 | 7.3473 | 7.389 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+440.00 | 9866311.3814 | 787167.0432 | 1885.825 | 1440 | 20 | 1881.681 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.665% | 1880.681 | 1 | 7.4643 | 7.506 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+460.00 | 9866323.8036 | 787151.3687 | 1885.965 | 1460 | 20 | 1881.546 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.7% | 1880.546 | 1 | 7.5993 | 7.641 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+480.00 | 9866336.2101 | 787135.6819 | 1886.103 | 1480 | 20 | 1881.429 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.69% | 1880.429 | 1 | 7.7163 | 7.758 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+500.00 | 9866348.5533 | 787119.9451 | 1886.237 | 1500 | 20 | 1881.323 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.67% | 1880.323 | 1 | 7.8223 | 7.864 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+520.00 | 9866360.8792 | 787104.1949 | 1886.373 | 1520 | 20 | 1881.217 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.68% | 1880.217 | 1 | 7.9283 | 7.97 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+540.00 | 9866373.1246 | 787088.3819 | 1886.519 | 1540 | 20 | 1881.108 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.73% | 1880.108 | 1 | 8.0373 | 8.079 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+560.00 | 9866385.4896 | 787072.6635 | 1886.653 | 1560 | 20 | 1880.998 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.67% | 1879.998 | 1 | 8.1473 | 8.189 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+580.00 | 9866398.0637 | 787057.1107 | 1886.765 | 1580 | 20 | 1880.885 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.56% | 1879.885 | 1 | 8.2603 | 8.302 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+600.00 | 9866410.5022 | 787041.4502 | 1886.875 | 1600 | 20 | 1880.778 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.55% | 1879.778 | 1 | 8.3673 | 8.409 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+620.00 | 9866422.7976 | 787025.676 | 1886.984 | 1620 | 20 | 1880.68 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.545% | 1879.68 | 1 | 8.4653 | 8.507 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+640.00 | 9866435.2081 | 787009.9929 | 1887.091 | 1640 | 20 | 1880.592 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.535% | 1879.592 | 1 | 8.5533 | 8.595 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+660.00 | 9866447.7293 | 786994.3974 | 1887.196 | 1660 | 20 | 1880.516 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.525% | 1879.516 | 1 | 8.6293 | 8.671 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+680.00 | 9866460.2062 | 786978.7668 | 1887.29 | 1680 | 20 | 1880.448 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.47% | 1879.448 | 1 | 8.6973 | 8.739 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+700.00 | 9866472.5721 | 786963.0478 | 1887.354 | 1700 | 20 | 1880.381 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.32% | 1879.381 | 1 | 8.7643 | 8.806 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+720.00 | 9866484.9063 | 786947.3041 | 1887.421 | 1720 | 20 | 1880.32 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.335% | 1879.32 | 1 | 8.8253 | 8.867 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+740.00 | 9866497.2059 | 786931.5332 | 1887.494 | 1740 | 20 | 1880.26 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.365% | 1879.26 | 1 | 8.8853 | 8.927 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+760.00 | 9866509.511 | 786915.7667 | 1887.547 | 1760 | 20 | 1880.221 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.265% | 1879.221 | 1 | 8.9243 | 8.966 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+780.00 | 9866521.8199 | 786900.003 | 1887.589 | 1780 | 20 | 1880.196 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.21% | 1879.196 | 1 | 8.9493 | 8.991 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+800.00 | 9866534.0891 | 786884.2086 | 1887.631 | 1800 | 20 | 1880.159 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.21% | 1879.159 | 1 | 8.9863 | 9.028 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+820.00 | 9866546.3317 | 786868.3934 | 1887.672 | 1820 | 20 | 1880.102 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.205% | 1879.102 | 1 | 9.0433 | 9.085 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+840.00 | 9866558.5673 | 786852.5729 | 1887.716 | 1840 | 20 | 1880.067 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.22% | 1879.067 | 1 | 9.0783 | 9.12 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+860.00 | 9866570.7853 | 786836.7387 | 1887.763 | 1860 | 20 | 1880.049 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.235% | 1879.049 | 1 | 9.0963 | 9.138 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+880.00 | 9866583.0719 | 786820.9581 | 1887.811 | 1880 | 20 | 1880.006 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.24% | 1879.006 | 1 | 9.1393 | 9.181 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+900.00 | 9866595.4638 | 786805.2597 | 1887.859 | 1900 | 20 | 1879.96 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.24% | 1878.96 | 1 | 9.1853 | 9.227 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+920.00 | 9866607.8611 | 786789.5655 | 1887.907 | 1920 | 20 | 1879.925 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.24% | 1878.925 | 1 | 9.2203 | 9.262 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+940.00 | 9866620.2937 | 786773.8993 | 1887.959 | 1940 | 20 | 1879.889 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.26% | 1878.889 | 1 | 9.2563 | 9.298 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+960.00 | 9866632.7263 | 786758.2331 | 1888.011 | 1960 | 20 | 1879.9 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.26% | 1878.9 | 1 | 9.2453 | 9.287 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 1+980.00 | 9866645.157 | 786742.5653 | 1888.051 | 1980 | 20 | 1879.902 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.2% | 1878.902 | 1 | 9.2433 | 9.285 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+000.00 | 9866657.5873 | 786726.8973 | 1888.089 | 2000 | 20 | 1879.692 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.19% | 1878.692 | 1 | 9.4533 | 9.495 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+020.00 | 9866669.9996 | 786711.215 | 1888.125 | 2020 | 20 | 1879.482 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.18% | 1878.482 | 1 | 9.6633 | 9.705 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+040.00 | 9866682.3763 | 786695.5046 | 1888.156 | 2040 | 20 | 1879.322 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.155% | 1878.322 | 1 | 9.8233 | 9.865 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+060.00 | 9866694.739 | 786679.7834 | 1888.187 | 2060 | 20 | 1879.234 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.155% | 1878.234 | 1 | 9.9113 | 9.953 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+080.00 | 9866706.768 | 786663.8052 | 1888.211 | 2080 | 20 | 1879.146 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.12% | 1878.146 | 1 | 9.9993 | 10.041 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+100.00 | 9866718.9436 | 786647.948 | 1888.222 | 2100 | 20 | 1879.058 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | 0.055% | 1878.058 | 1 | 10.0873 | 10.129 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+120.00 | 9866732.4822 | 786633.2271 | 1888.138 | 2120 | 20 | 1878.97 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.42% | 1877.97 | 1 | 10.1753 | 10.217 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+140.00 | 9866750.2544 | 786633.5956 | 1888.044 | 2140 | 20 | 1878.882 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.47% | 1877.882 | 1 | 10.2633 | 10.305 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+160.00 | 9866767.4951 | 786643.7317 | 1887.916 | 2160 | 20 | 1878.794 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.64% | 1877.794 | 1 | 10.3513 | 10.393 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+180.00 | 9866784.7818 | 786653.7897 | 1887.774 | 2180 | 20 | 1878.706 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.71% | 1877.706 | 1 | 10.4393 | 10.481 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+200.00 | 9866800.1112 | 786666.6274 | 1887.578 | 2200 | 20 | 1878.618 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.98% | 1877.618 | 1 | 10.5273 | 10.569 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+220.00 | 9866815.4096 | 786679.5084 | 1887.383 | 2220 | 20 | 1878.53 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.975% | 1877.53 | 1 | 10.6153 | 10.657 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+240.00 | 9866831.0631 | 786691.9571 | 1887.218 | 2240 | 20 | 1878.442 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.825% | 1877.442 | 1 | 10.7033 | 10.745 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+260.00 | 9866846.6737 | 786704.4584 | 1887.053 | 2260 | 20 | 1878.354 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.825% | 1877.354 | 1 | 10.7913 | 10.833 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+280.00 | 9866862.0463 | 786717.2523 | 1886.882 | 2280 | 20 | 1878.266 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.855% | 1877.266 | 1 | 10.8793 | 10.921 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+300.00 | 9866877.5851 | 786729.8302 | 1886.721 | 2300 | 20 | 1878.178 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.805% | 1877.178 | 1 | 10.9673 | 11.009 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+320.00 | 9866893.9381 | 786741.3445 | 1886.605 | 2320 | 20 | 1878.09 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.58% | 1877.09 | 1 | 11.0553 | 11.097 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+340.00 | 9866910.3713 | 786752.7394 | 1886.482 | 2340 | 20 | 1878.002 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.615% | 1877.002 | 1 | 11.1433 | 11.185 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+360.00 | 9866927.2381 | 786763.487 | 1886.318 | 2360 | 20 | 1877.914 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.82% | 1876.914 | 1 | 11.2313 | 11.273 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+380.00 | 9866944.1288 | 786774.1967 | 1886.15 | 2380 | 20 | 1877.826 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.84% | 1876.826 | 1 | 11.3193 | 11.361 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+400.00 | 9866961.0668 | 786784.8318 | 1885.976 | 2400 | 20 | 1877.738 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.87% | 1876.738 | 1 | 11.4073 | 11.449 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+420.00 | 9866978.3618 | 786794.8262 | 1885.81 | 2420 | 20 | 1877.65 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.83% | 1876.65 | 1 | 11.4953 | 11.537 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+440.00 | 9866996.3523 | 786803.5634 | 1885.657 | 2440 | 20 | 1877.562 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.765% | 1876.562 | 1 | 11.5833 | 11.625 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+460.00 | 9867014.4265 | 786812.1251 | 1885.464 | 2460 | 20 | 1877.474 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.965% | 1876.474 | 1 | 11.6713 | 11.713 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+480.00 | 9867032.5523 | 786820.578 | 1885.246 | 2480 | 20 | 1877.386 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -1.09% | 1876.386 | 1 | 11.7593 | 11.801 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+500.00 | 9867050.6954 | 786828.9941 | 1885.077 | 2500 | 20 | 1877.298 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.845% | 1876.298 | 1 | 11.8473 | 11.889 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+520.00 | 9867068.8452 | 786837.3954 | 1884.928 | 2520 | 20 | 1877.21 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.745% | 1876.21 | 1 | 11.9353 | 11.977 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+540.00 | 9867086.7464 | 786846.3118 | 1884.816 | 2540 | 20 | 1877.122 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.56% | 1876.122 | 1 | 12.0233 | 12.065 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+560.00 | 9867104.5898 | 786855.3433 | 1884.708 | 2560 | 20 | 1877.034 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.54% | 1876.034 | 1 | 12.1113 | 12.153 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+580.00 | 9867121.5562 | 786865.933 | 1884.492 | 2580 | 20 | 1876.946 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -1.08% | 1875.946 | 1 | 12.1993 | 12.241 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+600.00 | 9867138.981 | 786875.6807 | 1884.294 | 2600 | 20 | 1876.858 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.99% | 1875.858 | 1 | 12.2873 | 12.329 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+620.00 | 9867157.1182 | 786884.1093 | 1884.124 | 2620 | 20 | 1876.77 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.85% | 1875.77 | 1 | 12.3753 | 12.417 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+640.00 | 9867175.0435 | 786892.9758 | 1883.966 | 2640 | 20 | 1876.682 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.79% | 1875.682 | 1 | 12.4633 | 12.505 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+660.00 | 9867192.9048 | 786901.9742 | 1883.813 | 2660 | 20 | 1876.594 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.765% | 1875.594 | 1 | 12.5513 | 12.593 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+680.00 | 9867210.3269 | 786911.7944 | 1883.589 | 2680 | 20 | 1876.506 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -1.12% | 1875.506 | 1 | 12.6393 | 12.681 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+700.00 | 9867228.1538 | 786920.7202 | 1883.382 | 2700 | 20 | 1876.418 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -1.035% | 1875.418 | 1 | 12.7273 | 12.769 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+720.00 | 9867247.0958 | 786927.139 | 1883.232 | 2720 | 20 | 1876.33 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.75% | 1875.33 | 1 | 12.8153 | 12.857 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+740.00 | 9867266.0061 | 786933.6494 | 1883.071 | 2740 | 20 | 1876.242 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.805% | 1875.242 | 1 | 12.9033 | 12.945 | [5 empty] | 40 | 35.2 | 2.4 | PN 10
| 2+760.00 | 9867284.8706 | 786940.2927 | 1882.894 | 2760 | 20 | 1876.154 | 0.00087963 | 0.0352 | 0.00097265 | 0.90437 | 150 | 0.52661 | 0.041686 | 1888.187 | 1888.187 | 1888.1453 | -0.885% | 1875.154 | 1 | 12.9913 | 13.033 | [5 empty] | 40 | 35.2 | 2.4 | PN 10