## Survey Data
Station | Northing (m) | Easting (m) | Elevation (m) | Description
0+000.00 | 9869157.075 | 787472.264 | 1873.175 | Borehole
0+020.00 | 9869146.9267 | 787455.0355 | 1873.21 | Spotheight
0+040.00 | 9869135.8551 | 787438.381 | 1873.249 | Spotheight
0+060.00 | 9869124.9273 | 787421.6333 | 1873.356 | Spotheight
0+080.00 | 9869116.1636 | 787403.6666 | 1873.508 | Spotheight
0+100.00 | 9869106.5639 | 787386.1215 | 1873.635 | Spotheight
0+120.00 | 9869096.6369 | 787368.7632 | 1873.688 | Spotheight
0+140.00 | 9869086.3108 | 787351.6381 | 1873.754 | Spotheight
0+160.00 | 9869075.4645 | 787334.8542 | 1873.816 | Spotheight
0+180.00 | 9869064.9601 | 787317.8543 | 1873.865 | Spotheight
0+200.00 | 9869057.8535 | 787299.1809 | 1873.957 | Spotheight
0+220.00 | 9869051.6882 | 787280.1778 | 1873.98 | Spotheight
0+240.00 | 9869044.51 | 787261.5172 | 1873.995 | Spotheight
0+260.00 | 9869036.1064 | 787243.3976 | 1873.996 | Nkairowuani Kiosk 1
0+280.00 | 9869024.2022 | 787227.628 | 1873.997 | Spotheight
0+300.00 | 9869005.5321 | 787220.5775 | 1873.873 | Spotheight
0+320.00 | 9868986.0567 | 787216.0361 | 1873.725 | Spotheight
0+340.00 | 9868966.5553 | 787211.5982 | 1873.568 | Spotheight
0+360.00 | 9868946.9542 | 787207.6792 | 1873.397 | Spotheight
0+380.00 | 9868927.1914 | 787204.6078 | 1873.205 | Spotheight
0+400.00 | 9868907.747 | 787200.0786 | 1873.02 | Spotheight
0+420.00 | 9868888.5179 | 787194.5794 | 1872.841 | Spotheight
0+440.00 | 9868871.4438 | 787184.3609 | 1872.705 | Spotheight
0+460.00 | 9868854.5996 | 787173.6492 | 1872.573 | Spotheight
0+480.00 | 9868835.7443 | 787166.98 | 1872.385 | Spotheight
0+500.00 | 9868816.5621 | 787161.5966 | 1872.226 | Spotheight
0+520.00 | 9868796.775 | 787158.6866 | 1872.067 | Spotheight
0+540.00 | 9868777.8583 | 787153.1486 | 1871.927 | Spotheight
0+560.00 | 9868760.7253 | 787142.8305 | 1871.792 | Spotheight
0+580.00 | 9868742.7192 | 787134.2579 | 1871.663 | Spotheight
0+600.00 | 9868724.154 | 787126.8192 | 1871.516 | Spotheight
0+620.00 | 9868704.7627 | 787122.2944 | 1870.674 | Nkairowuani lagga
0+640.00 | 9868685.0949 | 787118.7909 | 1871.618 | Spotheight
0+660.00 | 9868665.1272 | 787117.6557 | 1871.598 | Spotheight
0+680.00 | 9868645.6318 | 787113.6606 | 1871.616 | Spotheight
0+700.00 | 9868626.4037 | 787108.1577 | 1871.653 | Spotheight
0+720.00 | 9868607.6465 | 787101.2543 | 1871.7 | Spotheight
0+740.00 | 9868588.9344 | 787094.2155 | 1871.749 | Spotheight
0+760.00 | 9868569.7319 | 787088.6242 | 1871.806 | Spotheight
0+780.00 | 9868550.7382 | 787082.4482 | 1871.907 | Spotheight
0+800.00 | 9868532.3948 | 787074.4783 | 1872.147 | Spotheight
0+820.00 | 9868513.5359 | 787068.0393 | 1872.325 | Spotheight
0+840.00 | 9868494.0731 | 787063.4348 | 1872.442 | Spotheight
0+860.00 | 9868474.3044 | 787060.6217 | 1872.6 | Spotheight
0+880.00 | 9868454.4113 | 787058.5565 | 1872.818 | Spotheight
0+900.00 | 9868434.5045 | 787056.6287 | 1872.957 | Spotheight
0+920.00 | 9868414.6117 | 787054.5917 | 1873.117 | Spotheight
0+940.00 | 9868394.8647 | 787051.421 | 1873.392 | Spotheight
0+960.00 | 9868375.0727 | 787048.6679 | 1873.659 | Spotheight
0+980.00 | 9868355.0957 | 787047.7095 | 1873.884 | Spotheight
1+000.00 | 9868335.1365 | 787046.5014 | 1874.113 | Spotheight
1+020.00 | 9868315.2273 | 787044.5972 | 1874.354 | Spotheight
1+040.00 | 9868295.3182 | 787042.6929 | 1874.552 | Spotheight
1+060.00 | 9868275.409 | 787040.7887 | 1874.701 | Spotheight
1+080.00 | 9868255.4999 | 787038.8844 | 1874.908 | Spotheight
1+100.00 | 9868235.588 | 787037.0148 | 1875.164 | Spotheight
1+120.00 | 9868215.6241 | 787035.8139 | 1875.371 | Spotheight
1+140.00 | 9868195.6615 | 787034.5953 | 1875.588 | Spotheight
1+160.00 | 9868175.7504 | 787032.7115 | 1875.835 | Spotheight
1+180.00 | 9868155.8536 | 787030.6967 | 1876.093 | Spotheight
1+200.00 | 9868136.005 | 787028.2409 | 1876.398 | Spotheight
1+220.00 | 9868116.0961 | 787026.3752 | 1876.613 | Spotheight
1+240.00 | 9868096.1599 | 787024.7785 | 1876.833 | Spotheight
1+260.00 | 9868076.2917 | 787022.5113 | 1877.068 | Spotheight
1+280.00 | 9868056.4411 | 787020.0717 | 1877.328 | Spotheight
1+300.00 | 9868036.5354 | 787018.1438 | 1877.547 | Spotheight
1+320.00 | 9868016.6189 | 787016.3189 | 1877.752 | Spotheight
1+340.00 | 9867996.6963 | 787014.5604 | 1877.925 | Spotheight
1+360.00 | 9867976.7717 | 787012.8259 | 1878.105 | Spotheight
1+380.00 | 9867956.8441 | 787011.1255 | 1878.325 | Spotheight
1+400.00 | 9867937.0649 | 787013.5657 | 1878.432 | Spotheight
1+420.00 | 9867917.5156 | 787017.6274 | 1878.519 | Spotheight
1+440.00 | 9867898.3739 | 787023.4233 | 1878.589 | Spotheight
1+460.00 | 9867879.5287 | 787030.0937 | 1878.669 | Spotheight
1+480.00 | 9867860.8159 | 787037.1527 | 1878.753 | Spotheight
1+500.00 | 9867841.5833 | 787042.5974 | 1878.876 | Spotheight
1+520.00 | 9867822.2674 | 787047.7819 | 1879.003 | Spotheight
1+540.00 | 9867803.1678 | 787053.7152 | 1879.077 | Spotheight
1+560.00 | 9867783.9946 | 787059.3291 | 1879.153 | Spotheight
1+580.00 | 9867764.0049 | 787058.7762 | 1879.261 | Spotheight
1+600.00 | 9867744.0207 | 787058.034 | 1879.376 | Spotheight
1+620.00 | 9867724.0762 | 787056.5446 | 1879.523 | Spotheight
1+640.00 | 9867704.2055 | 787054.4662 | 1879.674 | Spotheight
1+660.00 | 9867684.5246 | 787050.9079 | 1879.834 | Spotheight
1+680.00 | 9867664.7584 | 787047.9879 | 1879.991 | Spotheight
1+700.00 | 9867644.829 | 787046.308 | 1880.144 | Spotheight
1+720.00 | 9867624.9451 | 787044.2252 | 1880.287 | Spotheight
1+740.00 | 9867605.1445 | 787041.4079 | 1880.412 | Spotheight
1+760.00 | 9867585.331 | 787038.6945 | 1880.538 | Spotheight
1+780.00 | 9867565.4451 | 787036.561 | 1880.673 | Spotheight
1+800.00 | 9867545.5451 | 787034.6018 | 1880.804 | Spotheight
1+820.00 | 9867525.5723 | 787033.5608 | 1880.92 | Spotheight
1+840.00 | 9867505.6358 | 787032.2253 | 1881.038 | Spotheight
1+860.00 | 9867486.2931 | 787027.1401 | 1881.192 | Spotheight
1+880.00 | 9867467.0189 | 787021.8222 | 1881.345 | Spotheight
1+900.00 | 9867448.0196 | 787015.575 | 1881.495 | Spotheight
1+920.00 | 9867429.3258 | 787008.599 | 1881.641 | Spotheight
1+940.00 | 9867411.6804 | 786999.1843 | 1881.777 | Spotheight
1+960.00 | 9867393.8738 | 786990.0996 | 1881.923 | Spotheight
1+980.00 | 9867375.5743 | 786982.0295 | 1882.1 | Spotheight
2+000.00 | 9867357.1674 | 786974.2147 | 1882.264 | Spotheight
2+020.00 | 9867338.5957 | 786966.7923 | 1882.407 | Spotheight
2+040.00 | 9867320.2293 | 786958.9283 | 1882.556 | Spotheight
2+060.00 | 9867302.6497 | 786949.3911 | 1882.724 | Spotheight
2+080.00 | 9867284.8706 | 786940.2927 | 1882.894 | Spotheight
2+100.00 | 9867266.0061 | 786933.6494 | 1883.071 | Spotheight
2+120.00 | 9867247.0958 | 786927.139 | 1883.232 | Spotheight
2+140.00 | 9867228.1538 | 786920.7202 | 1883.382 | Spotheight
2+160.00 | 9867210.3269 | 786911.7944 | 1883.589 | Spotheight
2+180.00 | 9867192.9048 | 786901.9742 | 1883.813 | Spotheight
2+200.00 | 9867175.0435 | 786892.9758 | 1883.966 | Spotheight
2+220.00 | 9867157.1182 | 786884.1093 | 1884.124 | Spotheight
2+240.00 | 9867138.981 | 786875.6807 | 1884.294 | Spotheight
2+260.00 | 9867121.5562 | 786865.933 | 1884.492 | Spotheight
2+280.00 | 9867104.5898 | 786855.3433 | 1884.708 | Spotheight
2+300.00 | 9867086.7464 | 786846.3118 | 1884.816 | Spotheight
2+320.00 | 9867068.8452 | 786837.3954 | 1884.928 | Spotheight
2+340.00 | 9867050.6954 | 786828.9941 | 1885.077 | Spotheight
2+360.00 | 9867032.5523 | 786820.578 | 1885.246 | Spotheight
2+380.00 | 9867014.4265 | 786812.1251 | 1885.464 | Spotheight
2+400.00 | 9866996.3523 | 786803.5634 | 1885.657 | Spotheight
2+420.00 | 9866978.3618 | 786794.8262 | 1885.81 | Spotheight
2+440.00 | 9866961.0668 | 786784.8318 | 1885.976 | Spotheight
2+460.00 | 9866944.1288 | 786774.1967 | 1886.15 | Spotheight
2+480.00 | 9866927.2381 | 786763.487 | 1886.318 | Spotheight
2+500.00 | 9866910.3713 | 786752.7394 | 1886.482 | Spotheight
2+520.00 | 9866893.9381 | 786741.3445 | 1886.605 | Spotheight
2+540.00 | 9866877.5851 | 786729.8302 | 1886.721 | Spotheight
2+560.00 | 9866862.0463 | 786717.2523 | 1886.882 | Spotheight
2+580.00 | 9866846.6737 | 786704.4584 | 1887.053 | Spotheight
2+600.00 | 9866831.0631 | 786691.9571 | 1887.218 | Spotheight
2+620.00 | 9866815.4096 | 786679.5084 | 1887.383 | Spotheight
2+640.00 | 9866800.1112 | 786666.6274 | 1887.578 | Spotheight
2+660.00 | 9866784.7818 | 786653.7897 | 1887.774 | Spotheight
2+680.00 | 9866767.4951 | 786643.7317 | 1887.916 | Spotheight
2+700.00 | 9866750.2544 | 786633.5956 | 1888.044 | Spotheight
2+720.00 | 9866732.4822 | 786633.2271 | 1888.138 | Spotheight
2+740.00 | 9866718.9436 | 786647.948 | 1888.222 | Spotheight
2+760.00 | 9866706.768 | 786663.8052 | 1888.211 | Spotheight
2+780.00 | 9866694.739 | 786679.7834 | 1888.187 | Spotheight
2+800.00 | 9866682.3763 | 786695.5046 | 1888.156 | Spotheight
2+820.00 | 9866669.9996 | 786711.215 | 1888.125 | Spotheight
2+840.00 | 9866657.5873 | 786726.8973 | 1888.089 | Spotheight
2+860.00 | 9866645.157 | 786742.5653 | 1888.051 | Spotheight
2+880.00 | 9866632.7263 | 786758.2331 | 1888.011 | Spotheight
2+900.00 | 9866620.2937 | 786773.8993 | 1887.959 | Spotheight
2+920.00 | 9866607.8611 | 786789.5655 | 1887.907 | Spotheight
2+940.00 | 9866595.4638 | 786805.2597 | 1887.859 | Spotheight
2+960.00 | 9866583.0719 | 786820.9581 | 1887.811 | Spotheight
2+980.00 | 9866570.7853 | 786836.7387 | 1887.763 | Spotheight
3+000.00 | 9866558.5673 | 786852.5729 | 1887.716 | Spotheight
3+020.00 | 9866546.3317 | 786868.3934 | 1887.672 | Spotheight
3+040.00 | 9866534.0891 | 786884.2086 | 1887.631 | Spotheight
3+060.00 | 9866521.8199 | 786900.003 | 1887.589 | Spotheight
3+080.00 | 9866509.511 | 786915.7667 | 1887.547 | Spotheight
3+100.00 | 9866497.2059 | 786931.5332 | 1887.494 | Spotheight
3+120.00 | 9866484.9063 | 786947.3041 | 1887.421 | Spotheight
3+140.00 | 9866472.5721 | 786963.0478 | 1887.354 | Spotheight
3+160.00 | 9866460.2062 | 786978.7668 | 1887.29 | Spotheight
3+180.00 | 9866447.7293 | 786994.3974 | 1887.196 | Spotheight
3+200.00 | 9866435.2081 | 787009.9929 | 1887.091 | Spotheight
3+220.00 | 9866422.7976 | 787025.676 | 1886.984 | Spotheight
3+240.00 | 9866410.5022 | 787041.4502 | 1886.875 | Spotheight
3+260.00 | 9866398.0637 | 787057.1107 | 1886.765 | Spotheight
3+280.00 | 9866385.4896 | 787072.6635 | 1886.653 | Spotheight
3+300.00 | 9866373.1246 | 787088.3819 | 1886.519 | Spotheight
3+320.00 | 9866360.8792 | 787104.1949 | 1886.373 | Spotheight
3+340.00 | 9866348.5533 | 787119.9451 | 1886.237 | Spotheight
3+360.00 | 9866336.2101 | 787135.6819 | 1886.103 | Spotheight
3+380.00 | 9866323.8036 | 787151.3687 | 1885.965 | Spotheight
3+400.00 | 9866311.3814 | 787167.0432 | 1885.825 | Spotheight
3+420.00 | 9866299.0309 | 787182.774 | 1885.692 | Spotheight
3+440.00 | 9866286.7418 | 787198.553 | 1885.565 | Spotheight
3+460.00 | 9866274.2937 | 787214.2044 | 1885.431 | Spotheight
3+480.00 | 9866261.5326 | 787229.6041 | 1885.285 | Spotheight
3+500.00 | 9866247.8599 | 787244.1296 | 1885.156 | Spotheight
3+520.00 | 9866232.9471 | 787257.4566 | 1885.049 | Spotheight
3+540.00 | 9866215.957 | 787267.8011 | 1884.949 | Spotheight
3+560.00 | 9866198.2204 | 787277.043 | 1884.853 | Spotheight
3+580.00 | 9866179.9396 | 787285.1354 | 1884.775 | Spotheight
3+600.00 | 9866161.545 | 787292.9866 | 1884.701 | Spotheight
3+620.00 | 9866143.2519 | 787301.0708 | 1884.599 | Spotheight
3+640.00 | 9866124.9637 | 787309.1663 | 1884.494 | Spotheight
3+660.00 | 9866106.5345 | 787316.9356 | 1884.413 | Spotheight
3+680.00 | 9866088.2155 | 787324.9545 | 1884.329 | Spotheight
3+700.00 | 9866070.0665 | 787333.3576 | 1884.241 | Spotheight
3+720.00 | 9866051.8717 | 787341.6608 | 1884.162 | Spotheight
3+740.00 | 9866033.6517 | 787349.909 | 1884.055 | Spotheight
3+760.00 | 9866015.2999 | 787357.857 | 1883.987 | Spotheight
3+780.00 | 9865996.8987 | 787365.6924 | 1883.932 | Spotheight
3+800.00 | 9865978.4507 | 787373.4172 | 1883.838 | Spotheight
3+820.00 | 9865960.0007 | 787381.137 | 1883.741 | Spotheight
3+840.00 | 9865941.5758 | 787388.9166 | 1883.645 | Spotheight
3+860.00 | 9865923.1619 | 787396.7223 | 1883.549 | Spotheight
3+880.00 | 9865904.8333 | 787404.7242 | 1883.461 | Spotheight
3+900.00 | 9865886.565 | 787412.8648 | 1883.379 | Spotheight
3+920.00 | 9865868.6928 | 787421.767 | 1883.299 | Spotheight
3+940.00 | 9865851.5768 | 787432.1131 | 1883.224 | Spotheight
3+960.00 | 9865836.41 | 787444.8937 | 1883.123 | Spotheight
3+980.00 | 9865822.7297 | 787459.4832 | 1883.004 | Spotheight
4+000.00 | 9865808.5105 | 787473.54 | 1882.902 | Spotheight
4+020.00 | 9865794.0812 | 787487.389 | 1882.808 | Spotheight
4+040.00 | 9865779.5745 | 787501.1568 | 1882.695 | Spotheight
4+060.00 | 9865765.101 | 787514.9562 | 1882.578 | Spotheight
4+080.00 | 9865751.7685 | 787529.864 | 1882.463 | Spotheight
4+100.00 | 9865738.1967 | 787544.5385 | 1882.349 | Spotheight
4+120.00 | 9865723.5751 | 787558.1843 | 1882.237 | Spotheight
4+140.00 | 9865709.146 | 787572.0292 | 1882.122 | Spotheight
4+160.00 | 9865695.0236 | 787586.1911 | 1882.002 | Spotheight
4+180.00 | 9865680.9283 | 787600.3799 | 1881.894 | Spotheight
4+200.00 | 9865666.8615 | 787614.5969 | 1881.798 | Spotheight
4+220.00 | 9865652.5787 | 787628.5939 | 1881.681 | Spotheight
4+240.00 | 9865638.099 | 787642.3902 | 1881.546 | Spotheight
4+260.00 | 9865623.8519 | 787656.4238 | 1881.429 | Spotheight
4+280.00 | 9865609.7725 | 787670.6284 | 1881.323 | Spotheight
4+300.00 | 9865595.6099 | 787684.7485 | 1881.217 | Spotheight
4+320.00 | 9865581.1949 | 787698.6124 | 1881.108 | Spotheight
4+340.00 | 9865566.829 | 787712.5267 | 1880.998 | Spotheight
4+360.00 | 9865552.6077 | 787726.5892 | 1880.885 | Spotheight
4+380.00 | 9865538.3864 | 787740.6518 | 1880.778 | Spotheight
4+400.00 | 9865524.1652 | 787754.7143 | 1880.68 | Spotheight
4+420.00 | 9865509.7958 | 787768.6239 | 1880.592 | Spotheight
4+440.00 | 9865495.2795 | 787782.3817 | 1880.516 | Spotheight
4+460.00 | 9865480.9259 | 787796.3085 | 1880.448 | Spotheight
4+480.00 | 9865466.6257 | 787810.2907 | 1880.381 | Spotheight
4+500.00 | 9865452.2389 | 787824.1839 | 1880.32 | Spotheight
4+520.00 | 9865437.8323 | 787838.0565 | 1880.26 | Spotheight
4+540.00 | 9865423.3475 | 787851.8471 | 1880.221 | Spotheight
4+560.00 | 9865408.8115 | 787865.5841 | 1880.196 | Spotheight
4+580.00 | 9865394.405 | 787879.4545 | 1880.159 | Spotheight
4+600.00 | 9865380.2453 | 787893.579 | 1880.102 | Spotheight
4+620.00 | 9865365.8463 | 787907.4563 | 1880.067 | Spotheight
4+640.00 | 9865351.2658 | 787921.146 | 1880.049 | Spotheight
4+660.00 | 9865336.9408 | 787935.1021 | 1880.006 | Spotheight
4+680.00 | 9865322.6598 | 787949.104 | 1879.96 | Spotheight
4+700.00 | 9865307.8236 | 787962.5158 | 1879.925 | Spotheight
4+720.00 | 9865292.9776 | 787975.9171 | 1879.889 | Spotheight
4+740.00 | 9865278.5997 | 787989.8193 | 1879.9 | Spotheight
4+760.00 | 9865264.2386 | 788003.7387 | 1879.902 | Spotheight
4+780.00 | 9865250.1537 | 788017.9379 | 1879.692 | Spotheight
4+800.00 | 9865236.0689 | 788032.1371 | 1879.482 | Spotheight
4+820.00 | 9865222.018 | 788046.3699 | 1879.322 | Spotheight
4+832.87 | 9865212.989 | 788055.536 | 1879.234 | Nkairowuani Kiosk 2

## Water Demand
Item | Units
B.H Yield | 9.5 | m³/Hr
Population Targeted | 2500 | people
Water demand per capita | 20 | L/d/p
Total Water Demand per day | 50000 | Litres
Reservoir capacity required (tank) | 50 | m³
Reservoir | 100 | m³
Unmet Demand | -50 | m³
Note:
20 litres per capita per day should be assured to take care of basic hygiene needs and basic food hygiene (WHO)
Assumption: | 1 day | 8 hrs | Pump operational for10 hrs

## Pump Design
BOREHOLE DATA
BH depth (m) = | 200 | Max Disccharge | Pump Operational Factor of Safety
Pump level present (m) = | 187
Yield (m3/hr) = | 6 | 4 | 66.67%
HEAD CALCULATIIONS
Pump level |  |  | 187
Frictional Losses |  |  | 12.5921
delivery head |  |  | 50
Tank height |  |  | 1.5
Residual head | 15% |  | 9.6138
Total Head |  |  | 260.706
POWER REQUIREMENT
H (m) | Q (L/Sec) | Constant | Pump efficiency |  | KW
260.706 | 1.1111 | 102 | 0.65 |  | 4.3691
Add factor safety |  |  | 1.5 | 6.5537 | KW
|  |  |  | 8.1921 | KVA
PUMP RECOMMENDATIONS
Dayliff DS 5/60 | Power | 5.5 Kw
| Discharge | m3/hr | Head | m
| Min Q | 3 | Hmax | 310
| Max Q | 6 | Hmin | 260
Grundfos SP 5A - 75 | Power | 7.5 Kw
| Discharge | m3/hr | Head | m
| Min Q | 3 | Hmax | 390
| Max Q | 6 | Hmin | 210
Insert Alternative C | Power
| Discharge | m3/hr | Head | m
| Min Q |  | Hmax
| Max Q |  | Hmin

## Rising Main - Tank
NKAIRUWANI WATER PROJECT |  |  |  |  | 1000000
Contract No.: | [17 empty] | Soil Cover | 1 |  | Assumption: | Discharge | 0.0011111
Profile levels - end of line included
Date:12.12.2021 | [27 empty] | Pipe Details
Nodes | Station | Northing(m) | Easting(m) | Elevation(m) | Chainage | Length (m) | Orig. Ground Level | Discharge (m3/s) | Internal diameter (m) | Area (m2) | Velocity (m/s) | C | HL | Vf | El Static | EL | HGL | Slope (%) | Pipe invert (m) | Depth of excavation (m) | Hp | Hs | Off-take (m3/s) | Total flow (m3/s) | Bends | Losses due to bends | Remarks | External Diameter (mm) | Internal Diameter (mm) | Wall Thickness (mm) | Class | Soil Type
| 0+000 | 9876483.456 | 687489.803 | 1535.24 | 0 | 0 | 1873.175 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0 | 0.027244 | 1876.5441 | 1876.5441 | 1876.5169 |  | 1872.175 | 1 | 4.3419 | 4.3691 |  | 0.0011111 |  |  | Borehole | 50 | 44 | 3 | PN 10.0
| 0+020 | 9876484.177 | 687505.198 | 1535.884 | 20 | 20 | 1873.21 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1876.2704 | 1876.2431 | 3.22% | 1872.21 | 1 | 4.0331 | 4.3341 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+040 | 9876487.792 | 687521.023 | 1536.887 | 40 | 20 | 1873.249 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1875.9966 | 1875.9694 | 5.015% | 1872.249 | 1 | 3.7204 | 4.2951 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+060 | 9876482.571 | 687525.22 | 1537.039 | 60 | 20 | 1873.356 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1875.7229 | 1875.6957 | 0.76% | 1872.356 | 1 | 3.3397 | 4.1881 |  |  |  |  | church | 50 | 44 | 3 | PN 10.0
| 0+080 | 9876483.11 | 687537.915 | 1537.581 | 80 | 20 | 1873.508 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1875.4492 | 1875.4219 | 2.71% | 1872.508 | 1 | 2.9139 | 4.0361 |  |  |  |  | church | 50 | 44 | 3 | PN 10.0
| 0+100 | 9876476.372 | 687538.098 | 1537.586 | 100 | 20 | 1873.635 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1875.1754 | 1875.1482 | 0.025% | 1872.635 | 1 | 2.5132 | 3.9091 |  |  |  |  | church | 50 | 44 | 3 | PN 10.0
| 0+120 | 9876488.907 | 687537.826 | 1537.796 | 120 | 20 | 1873.688 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1874.9017 | 1874.8744 | 1.05% | 1872.688 | 1 | 2.1864 | 3.8561 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+140 | 9876490.445 | 687553.552 | 1538.606 | 140 | 20 | 1873.754 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1874.6279 | 1874.6007 | 4.05% | 1872.754 | 1 | 1.8467 | 3.7901 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+160 | 9876490.146 | 687571.224 | 1539.755 | 160 | 20 | 1873.816 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1874.3542 | 1874.3269 | 5.745% | 1872.816 | 1 | 1.5109 | 3.7281 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+180 | 9876487.435 | 687588.32 | 1540.739 | 180 | 20 | 1873.865 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1874.0804 | 1874.0532 | 4.92% | 1872.865 | 1 | 1.1882 | 3.6791 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+200 | 9876495.244 | 687583.387 | 1540.812 | 200 | 20 | 1873.957 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1873.8067 | 1873.7795 | 0.365% | 1872.957 | 1 | 0.82246 | 3.5871 |  |  |  |  | house | 50 | 44 | 3 | PN 10.0
| 0+220 | 9876495.274 | 687588.034 | 1541.008 | 220 | 20 | 1873.98 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1873.533 | 1873.5057 | 0.98% | 1872.98 | 1 | 0.52572 | 3.5641 |  |  |  |  | house | 50 | 44 | 3 | PN 10.0
| 0+240 | 9876486.899 | 687604.025 | 1541.724 | 240 | 20 | 1873.995 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1873.2592 | 1873.232 | 3.58% | 1872.995 | 1 | 0.23698 | 3.5491 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+260 | 9876488.034 | 687598.039 | 1541.27 | 260 | 20 | 1873.996 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1872.9855 | 1872.9582 | -2.27% | 1872.996 | 1 | -0.037763 | 3.5481 |  |  |  |  | Road CL | 50 | 44 | 3 | PN 10.0
| 0+280 | 9876495.153 | 687622.635 | 1543.062 | 280 | 20 | 1873.997 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1872.7117 | 1872.6845 | 8.96% | 1872.997 | 1 | -0.31251 | 3.5471 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+300 | 9876492.752 | 687605.364 | 1541.907 | 300 | 20 | 1873.873 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1872.438 | 1872.4108 | -5.775% | 1872.873 | 1 | -0.46225 | 3.6711 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+320 | 9876496.12 | 687637.687 | 1543.887 | 320 | 20 | 1873.725 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1872.1643 | 1872.137 | 9.9% | 1872.725 | 1 | -0.58799 | 3.8191 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+340 | 9876496.407 | 687655.501 | 1544.956 | 340 | 20 | 1873.568 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1871.8905 | 1871.8633 | 5.345% | 1872.568 | 1 | -0.70473 | 3.9761 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+360 | 9876498.455 | 687669.949 | 1545.832 | 360 | 20 | 1873.397 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1871.6168 | 1871.5895 | 4.38% | 1872.397 | 1 | -0.80747 | 4.1471 |  |  |  |  | fence | 50 | 44 | 3 | PN 10.0
| 0+380 | 9876498.723 | 687674.623 | 1546.049 | 380 | 20 | 1873.205 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1871.343 | 1871.3158 | 1.085% | 1872.205 | 1 | -0.88922 | 4.3391 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+400 | 9876503.479 | 687693.494 | 1547.528 | 400 | 20 | 1873.02 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1871.0693 | 1871.042 | 7.395% | 1872.02 | 1 | -0.97796 | 4.5241 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+420 | 9876507.191 | 687712.187 | 1548.911 | 420 | 20 | 1872.841 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1870.7955 | 1870.7683 | 6.915% | 1871.841 | 1 | -1.0727 | 4.7031 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+440 | 9876511.79 | 687730.985 | 1550.351 | 440 | 20 | 1872.705 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1870.5218 | 1870.4946 | 7.2% | 1871.705 | 1 | -1.2104 | 4.8391 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+460 | 9876515.873 | 687749.448 | 1551.94 | 460 | 20 | 1872.573 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1870.2481 | 1870.2208 | 7.945% | 1871.573 | 1 | -1.3522 | 4.9711 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+480 | 9876516.033 | 687751.336 | 1552.073 | 480 | 20 | 1872.385 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1869.9743 | 1869.9471 | 0.665% | 1871.385 | 1 | -1.4379 | 5.1591 |  |  |  |  | maize plant | 50 | 44 | 3 | PN 10.0
| 0+500 | 9876519.097 | 687770.012 | 1553.625 | 500 | 20 | 1872.226 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1869.7006 | 1869.6733 | 7.76% | 1871.226 | 1 | -1.5527 | 5.3181 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+520 | 9876523.412 | 687790.391 | 1555.409 | 520 | 20 | 1872.067 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1869.4268 | 1869.3996 | 8.92% | 1871.067 | 1 | -1.6674 | 5.4771 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+540 | 9876528.219 | 687810.971 | 1557.245 | 540 | 20 | 1871.927 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1869.1531 | 1869.1258 | 9.18% | 1870.927 | 1 | -1.8012 | 5.6171 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+560 | 9876534.546 | 687832.269 | 1559.133 | 560 | 20 | 1871.792 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1868.8793 | 1868.8521 | 9.44% | 1870.792 | 1 | -1.9399 | 5.7521 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+580 | 9876535.773 | 687836.836 | 1559.49 | 580 | 20 | 1871.663 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1868.6056 | 1868.5784 | 1.785% | 1870.663 | 1 | -2.0846 | 5.8811 |  |  |  |  | maize plants | 50 | 44 | 3 | PN 10.0
| 0+600 | 9876538.423 | 687842.668 | 1560.187 | 600 | 20 | 1871.516 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1868.3319 | 1868.3046 | 5.27% | 1870.516 | 1 | -2.2114 | 6.0281 |  |  |  |  | road | 50 | 44 | 3 | PN 10.0
| 0+620 | 9876545.814 | 687857.797 | 1561.946 | 620 | 20 | 1870.674 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1868.0581 | 1868.0309 | 12.28% | 1869.674 | 1 | -1.6431 | 6.8701 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+640 | 9876554.139 | 687876.112 | 1564.141 | 640 | 20 | 1871.618 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1867.7844 | 1867.7571 | 19.77% | 1870.618 | 1 | -2.8609 | 5.9261 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+660 | 9876557.853 | 687875.464 | 1564.454 | 660 | 20 | 1871.598 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1867.5106 | 1867.4834 | 12.54% | 1870.598 | 1 | -3.1146 | 5.9461 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+680 | 9876567.022 | 687892.575 | 1566.562 | 680 | 20 | 1871.616 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1867.2369 | 1867.2096 | 12.1% | 1870.616 | 1 | -3.4064 | 5.9281 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+700 | 9876568.248 | 687895.388 | 1566.916 | 700 | 20 | 1871.653 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1866.9632 | 1866.9359 | 12.31% | 1870.653 | 1 | -3.7171 | 5.8911 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+720 | 9876575.52 | 687912.532 | 1569.864 | 720 | 20 | 1871.7 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1866.6894 | 1866.6622 | 16.51% | 1870.7 | 1 | -4.0378 | 5.8441 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+740 | 9876583.432 | 687930.105 | 1573.453 | 740 | 20 | 1871.749 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1866.4157 | 1866.3884 | 32.69% | 1870.749 | 1 | -4.3606 | 5.7951 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+760 | 9876588.508 | 687946.45 | 1577.047 | 760 | 20 | 1871.806 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1866.1419 | 1866.1147 | 35.91% | 1870.806 | 1 | -4.6913 | 5.7381 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+780 | 9876588.235 | 687946.869 | 1577.15 | 780 | 20 | 1871.907 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1865.8682 | 1865.8409 | 18.49% | 1870.907 | 1 | -5.0661 | 5.6371 |  |  |  |  | fence | 50 | 44 | 3 | PN 10.0
| 0+800 | 9876591.762 | 687947.967 | 1577.635 | 800 | 20 | 1872.147 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1865.5944 | 1865.5672 | 2.94% | 1871.147 | 1 | -5.5798 | 5.3971 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+820 | 9876598.226 | 687964.56 | 1582.282 | 820 | 20 | 1872.325 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1865.3207 | 1865.2935 | 25.66% | 1871.325 | 1 | -6.0315 | 5.2191 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+840 | 9876599.282 | 687984.207 | 1588.142 | 840 | 20 | 1872.442 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1865.047 | 1865.0197 | 52.54% | 1871.442 | 1 | -6.4223 | 5.1021 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+860 | 9876615.426 | 688000.415 | 1595.421 | 860 | 20 | 1872.6 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1864.7732 | 1864.746 | 65.7% | 1871.6 | 1 | -6.854 | 4.9441 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+880 | 9876624.023 | 688013.015 | 1600.917 | 880 | 20 | 1872.818 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1864.4995 | 1864.4722 | 63.87% | 1871.818 | 1 | -7.3458 | 4.7261 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+900 | 9876630.157 | 688029.516 | 1607.735 | 900 | 20 | 1872.957 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1864.2257 | 1864.1985 | 61.57% | 1871.957 | 1 | -7.7585 | 4.5871 |  |  |  |  | pipeline route | 50 | 44 | 3 | PN 10.0
| 0+920 | 9876638.891 | 688038.386 | 1609.969 | 920 | 20 | 1873.117 | 0.0011111 | 0.044 | 0.0015198 | 0.73111 | 150 | 0.27374 | 0.027244 | 1876.5441 | 1863.952 | 1863.9247 | 45.26% | 1872.117 | 1 | -8.1923 | 4.4271 | [5 empty] | 50 | 44 | 3 | PN 10.0
12.5921

## Dist - Tank to WK 1
NKAIRUWANI WATER SUPPLY PROJECT
Contract No.: | [17 empty] | Soil Cover | 1 |  | Assumption: | Discharge | 0.00046296
Profile levels - end of line included
Date: 21.12.2021 | [27 empty] | Pipe Details
Nodes | Station | Northing(m) | Easting(m) | Elevation(m) | Chainage | Length (m) | Orig. Ground Level | Discharge (m3/s) | Internal diameter (m) | Area (m2) | Velocity (m/s) | C | HL | Vf | El Static | EL | HGL | Slope (%) | Pipe invert (m) | Depth of excavation (m) | Hp | Hs | Off-take (m3/s) | Total flow (m3/s) | Bends | Losses due to bends | Remarks | External Diameter (mm) | Internal Diameter (mm) | Wall Thickness (mm) | Class | Soil Type
| 0+000 | 9876639.21 | 688047.569 | 1610.936 | 0 | 0 | 1888.187 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 |  | 1887.187 | 1 | -0.028842 | 0 |  | 0.00046296 |  |  | tank site | 32 | 28 | 2 | PN 10
| 0+020 | 9876631.62 | 688043.667 | 1609.456 | 20 | 20 | 1888.156 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -7.4% | 1887.156 | 1 | 0.0021582 | 0.031 |  |  |  |  | tank site | 32 | 28 | 2 | PN 10
| 0+040 | 9876638.891 | 688038.386 | 1609.969 | 40 | 20 | 1888.125 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 2.565% | 1887.125 | 1 | 0.033158 | 0.062 |  |  |  |  | tank site | 32 | 28 | 2 | PN 10
| 0+060 | 9876630.157 | 688029.516 | 1607.735 | 60 | 20 | 1888.089 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -11.17% | 1887.089 | 1 | 0.069158 | 0.098 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+080 | 9876624.023 | 688013.015 | 1600.917 | 80 | 20 | 1888.051 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -34.09% | 1887.051 | 1 | 0.10716 | 0.136 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+100 | 9876615.426 | 688000.415 | 1595.421 | 100 | 20 | 1888.011 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -27.48% | 1887.011 | 1 | 0.14716 | 0.176 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+120 | 9876599.282 | 687984.207 | 1588.142 | 120 | 20 | 1887.959 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -36.39% | 1886.959 | 1 | 0.19916 | 0.228 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+140 | 9876598.226 | 687964.56 | 1582.282 | 140 | 20 | 1887.907 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -29.3% | 1886.907 | 1 | 0.25116 | 0.28 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+160 | 9876591.762 | 687947.967 | 1577.635 | 160 | 20 | 1887.859 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -23.23% | 1886.859 | 1 | 0.29916 | 0.328 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+180 | 9876588.508 | 687946.45 | 1577.047 | 180 | 20 | 1887.811 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -2.94% | 1886.811 | 1 | 0.34716 | 0.376 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+200 | 9876583.432 | 687930.105 | 1573.453 | 200 | 20 | 1887.763 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -17.97% | 1886.763 | 1 | 0.39516 | 0.424 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+220 | 9876575.52 | 687912.532 | 1569.864 | 220 | 20 | 1887.716 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -17.94% | 1886.716 | 1 | 0.44216 | 0.471 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+240 | 9876568.248 | 687895.388 | 1566.916 | 240 | 20 | 1887.672 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -14.74% | 1886.672 | 1 | 0.48616 | 0.515 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+260 | 9876567.022 | 687892.575 | 1566.562 | 260 | 20 | 1887.631 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -1.77% | 1886.631 | 1 | 0.52716 | 0.556 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+280 | 9876557.853 | 687875.464 | 1564.454 | 280 | 20 | 1887.589 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -10.54% | 1886.589 | 1 | 0.56916 | 0.598 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+300 | 9876554.139 | 687876.112 | 1564.141 | 300 | 20 | 1887.547 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -1.565% | 1886.547 | 1 | 0.61116 | 0.64 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+320 | 9876545.814 | 687857.797 | 1561.946 | 320 | 20 | 1887.494 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -10.98% | 1886.494 | 1 | 0.66416 | 0.693 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+340 | 9876538.423 | 687842.668 | 1560.187 | 340 | 20 | 1887.421 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -8.795% | 1886.421 | 1 | 0.73716 | 0.766 |  |  |  |  | road | 32 | 28 | 2 | PN 10
| 0+360 | 9876535.773 | 687836.836 | 1559.49 | 360 | 20 | 1887.354 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -3.485% | 1886.354 | 1 | 0.80416 | 0.833 |  |  |  |  | maize plants | 32 | 28 | 2 | PN 10
| 0+380 | 9876534.546 | 687832.269 | 1559.133 | 380 | 20 | 1887.29 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -1.785% | 1886.29 | 1 | 0.86816 | 0.897 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+400 | 9876528.219 | 687810.971 | 1557.245 | 400 | 20 | 1887.196 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -9.44% | 1886.196 | 1 | 0.96216 | 0.991 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+420 | 9876523.412 | 687790.391 | 1555.409 | 420 | 20 | 1887.091 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -9.18% | 1886.091 | 1 | 1.0672 | 1.096 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+440 | 9876519.097 | 687770.012 | 1553.625 | 440 | 20 | 1886.984 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -8.92% | 1885.984 | 1 | 1.1742 | 1.203 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+460 | 9876516.033 | 687751.336 | 1552.073 | 460 | 20 | 1886.875 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -7.76% | 1885.875 | 1 | 1.2832 | 1.312 |  |  |  |  | maize plant | 32 | 28 | 2 | PN 10
| 0+480 | 9876515.873 | 687749.448 | 1551.94 | 480 | 20 | 1886.765 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -0.665% | 1885.765 | 1 | 1.3932 | 1.422 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+500 | 9876511.79 | 687730.985 | 1550.351 | 500 | 20 | 1886.653 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -7.945% | 1885.653 | 1 | 1.5052 | 1.534 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+520 | 9876507.191 | 687712.187 | 1548.911 | 520 | 20 | 1886.519 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -7.2% | 1885.519 | 1 | 1.6392 | 1.668 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+540 | 9876503.479 | 687693.494 | 1547.528 | 540 | 20 | 1886.373 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -6.915% | 1885.373 | 1 | 1.7852 | 1.814 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+560 | 9876498.723 | 687674.623 | 1546.049 | 560 | 20 | 1886.237 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -7.395% | 1885.237 | 1 | 1.9212 | 1.95 | 0 |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+580 | 9876498.455 | 687669.949 | 1545.832 | 580 | 20 | 1886.103 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -1.085% | 1885.103 | 1 | 2.0552 | 2.084 |  |  |  |  | fence | 32 | 28 | 2 | PN 10
| 0+600 | 9876496.407 | 687655.501 | 1544.956 | 600 | 20 | 1885.965 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -4.38% | 1884.965 | 1 | 2.1932 | 2.222 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10 |  | 22.5
| 0+620 | 9876496.12 | 687637.687 | 1543.887 | 620 | 20 | 1885.825 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -5.345% | 1884.825 | 1 | 2.3332 | 2.362 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+640 | 9876492.752 | 687605.364 | 1541.907 | 640 | 20 | 1885.692 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -9.9% | 1884.692 | 1 | 2.4662 | 2.495 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+660 | 9876495.153 | 687622.635 | 1543.062 | 660 | 20 | 1885.565 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 5.775% | 1884.565 | 1 | 2.5932 | 2.622 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+680 | 9876499.13 | 687601.876 | 1541.459 | 680 | 20 | 1885.431 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -8.015% | 1884.431 | 1 | 2.7272 | 2.756 |  |  |  |  | t-junction | 32 | 28 | 2 | PN 10
| 0+700 | 9876531.524 | 687600.933 | 1541.697 | 700 | 20 | 1885.285 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 1.19% | 1884.285 | 1 | 2.8732 | 2.902 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+720 | 9876546.23 | 687599.802 | 1541.903 | 720 | 20 | 1885.156 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 1.03% | 1884.156 | 1 | 3.0022 | 3.031 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+740 | 9876568.243 | 687599.301 | 1542.183 | 740 | 20 | 1885.049 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 1.4% | 1884.049 | 1 | 3.1092 | 3.138 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+760 | 9876587.158 | 687601.494 | 1542.359 | 760 | 20 | 1884.949 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 0.88% | 1883.949 | 1 | 3.2092 | 3.238 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+780 | 9876603.273 | 687603.752 | 1542.677 | 780 | 20 | 1884.853 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 1.59% | 1883.853 | 1 | 3.3052 | 3.334 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+800 | 9876618.513 | 687606.598 | 1543.1 | 800 | 20 | 1884.775 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 2.115% | 1883.775 | 1 | 3.3832 | 3.412 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+820 | 9876636.262 | 687610.902 | 1543.613 | 820 | 20 | 1884.701 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 2.565% | 1883.701 | 1 | 3.4572 | 3.486 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+840 | 9876661.087 | 687618.859 | 1544.504 | 840 | 20 | 1884.599 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 4.455% | 1883.599 | 1 | 3.5592 | 3.588 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+860 | 9876685.313 | 687627.363 | 1545.434 | 860 | 20 | 1884.494 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 4.65% | 1883.494 | 1 | 3.6642 | 3.693 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+880 | 9876715.442 | 687636.999 | 1546.694 | 880 | 20 | 1884.413 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 6.3% | 1883.413 | 1 | 3.7452 | 3.774 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+900 | 9876735.869 | 687643.614 | 1547.381 | 900 | 20 | 1884.329 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 3.435% | 1883.329 | 1 | 3.8292 | 3.858 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+920 | 9876764.373 | 687652.46 | 1548.36 | 920 | 20 | 1884.241 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 4.895% | 1883.241 | 1 | 3.9172 | 3.946 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+940 | 9876793.987 | 687662.89 | 1549.454 | 940 | 20 | 1884.162 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 5.47% | 1883.162 | 1 | 3.9962 | 4.025 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+960 | 9876819.699 | 687672.017 | 1550.532 | 960 | 20 | 1884.055 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 5.39% | 1883.055 | 1 | 4.1032 | 4.132 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+980 | 9876852.467 | 687682.931 | 1551.875 | 980 | 20 | 1883.987 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 6.715% | 1882.987 | 1 | 4.1712 | 4.2 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+1000 | 9876877.718 | 687691.923 | 1552.712 | 1000 | 20 | 1883.932 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 4.185% | 1882.932 | 1 | 4.2262 | 4.255 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+1020 | 9876901.203 | 687700.278 | 1553.776 | 1020 | 20 | 1883.838 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 5.32% | 1882.838 | 1 | 4.3202 | 4.349 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 8
| 0+1040 | 9876934.716 | 687712.226 | 1555.512 | 1040 | 20 | 1883.741 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 8.68% | 1882.741 | 1 | 4.4172 | 4.446 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 8
| 0+1060 | 9876962.335 | 687721.76 | 1557.119 | 1060 | 20 | 1883.645 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 8.035% | 1882.645 | 1 | 4.5132 | 4.542 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 8
| 0+1080 | 9876978.754 | 687727.536 | 1557.89 | 1080 | 20 | 1883.549 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 3.855% | 1882.549 | 1 | 4.6092 | 4.638 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 8
| 0+1100 | 9876999.053 | 687733.695 | 1559.321 | 1100 | 20 | 1883.461 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 7.155% | 1882.461 | 1 | 4.6972 | 4.726 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 8
| 0+1120 | 9877020.182 | 687740.489 | 1561.126 | 1120 | 20 | 1883.379 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 9.025% | 1882.379 | 1 | 4.7792 | 4.808 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 8
| 0+1140 | 9877041.757 | 687746.672 | 1562.736 | 1140 | 20 | 1883.299 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 8.05% | 1882.299 | 1 | 4.8592 | 4.888 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 8
| 0+1160 | 9877063.78 | 687753.245 | 1564.901 | 1160 | 20 | 1883.224 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 10.82% | 1882.224 | 1 | 4.9342 | 4.963 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 8
| 0+1180 | 9877085.387 | 687758.97 | 1567.155 | 1180 | 20 | 1883.123 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 11.27% | 1882.123 | 1 | 5.0352 | 5.064 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 8
| 0+1200 | 9877106.922 | 687763.891 | 1569.206 | 1200 | 20 | 1883.004 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 10.25% | 1882.004 | 1 | 5.1542 | 5.183 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 8
| 0+1220 | 9877128.712 | 687767.464 | 1570.972 | 1220 | 20 | 1882.902 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 8.83% | 1881.902 | 1 | 5.2562 | 5.285 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 8
| 0+1240 | 9877149.947 | 687773.12 | 1572.058 | 1240 | 20 | 1882.808 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 5.43% | 1881.808 | 1 | 5.3502 | 5.379 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 8
| 0+1260 | 9877170.979 | 687778.287 | 1572.652 | 1260 | 20 | 1882.695 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 2.97% | 1881.695 | 1 | 5.4632 | 5.492 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 8
| 0+1280 | 9877191.679 | 687784.297 | 1573.277 | 1280 | 20 | 1882.578 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 3.125% | 1881.578 | 1 | 5.5802 | 5.609 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 8
| 0+1300 | 9877212.167 | 687790.195 | 1574.092 | 1300 | 20 | 1882.463 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 4.075% | 1881.463 | 1 | 5.6952 | 5.724 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 8
| 0+1320 | 9877233.192 | 687796.877 | 1575.374 | 1320 | 20 | 1882.349 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 6.41% | 1881.349 | 1 | 5.8092 | 5.838 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 8
| 0+1340 | 9877253.459 | 687804.808 | 1576.777 | 1340 | 20 | 1882.237 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 7.015% | 1881.237 | 1 | 5.9212 | 5.95 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 8
| 0+1360 | 9877276.608 | 687814.614 | 1577.797 | 1360 | 20 | 1882.122 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 5.1% | 1881.122 | 1 | 6.0362 | 6.065 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 8
| 0+1380 | 9877297.763 | 687820.705 | 1578.326 | 1380 | 20 | 1882.002 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 2.645% | 1881.002 | 1 | 6.1562 | 6.185 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 8
| 0+1400 | 9877318.224 | 687826.618 | 1578.836 | 1400 | 20 | 1881.894 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 2.55% | 1880.894 | 1 | 6.2642 | 6.293 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 8
| 0+1420 | 9877338.048 | 687832.828 | 1579.34 | 1420 | 20 | 1881.798 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 2.52% | 1880.798 | 1 | 6.3602 | 6.389 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 8
| 0+1440 | 9877356.972 | 687839.285 | 1579.908 | 1440 | 20 | 1881.681 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 2.84% | 1880.681 | 1 | 6.4772 | 6.506 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 8
| 0+1460 | 9877375.928 | 687847.188 | 1580.574 | 1460 | 20 | 1881.546 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 3.33% | 1880.546 | 1 | 6.6122 | 6.641 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 8
| 0+1480 | 9877396.342 | 687855.829 | 1581.204 | 1480 | 20 | 1881.429 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 3.15% | 1880.429 | 1 | 6.7292 | 6.758 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 8
| 0+1500 | 9877415.737 | 687864.713 | 1582.545 | 1500 | 20 | 1881.323 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 6.705% | 1880.323 | 1 | 6.8352 | 6.864 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 8
| 0+1520 | 9877411.883 | 687877.873 | 1584.831 | 1520 | 20 | 1881.217 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 11.43% | 1880.217 | 1 | 6.9412 | 6.97 |  |  |  |  | tank site | 32 | 28 | 2 | PN 8
| 0+1540 | 9877413.182 | 687872.924 | 1584.199 | 1540 | 20 | 1881.108 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -3.16% | 1880.108 | 1 | 7.0502 | 7.079 |  |  |  |  | tank site | 32 | 28 | 2 | PN 8
| 0+1560 | 9877407.225 | 687871.924 | 1583.957 | 1560 | 20 | 1880.998 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -1.21% | 1879.998 | 1 | 7.1602 | 7.189 |  |  |  |  | tank site | 32 | 28 | 2 | PN 8

## Return - Tank to WK 3
NKAIRUWANI WATER SUPPLY PROJECT
Contract No.: | [17 empty] | Soil Cover | 1 |  | Assumption: | Discharge | 0.00046296
Profile levels - end of line included
Date: 21.12.2021 | [27 empty] | Pipe Details
Nodes | Station | Northing(m) | Easting(m) | Elevation(m) | Chainage | Length (m) | Orig. Ground Level | Discharge (m3/s) | Internal diameter (m) | Area (m2) | Velocity (m/s) | C | HL | Vf | El Static | EL | HGL | Slope (%) | Pipe invert (m) | Depth of excavation (m) | Hp | Hs | Off-take (m3/s) | Total flow (m3/s) | Bends | Losses due to bends | Remarks | External Diameter (mm) | Internal Diameter (mm) | Wall Thickness (mm) | Class | Soil Type
| 0+000.00 | 9876639.21 | 688047.569 | 1610.936 | 0 | 0 | 1888.187 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 |  | 1887.187 | 1 | -0.028842 | 0 |  | 0.00046296 |  |  | tank site | 32 | 28 | 2 | PN 10
| 0+020.00 | 9876631.62 | 688043.667 | 1609.456 | 20 | 20 | 1888.156 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -7.4% | 1887.156 | 1 | 0.0021582 | 0.031 |  |  |  |  | tank site | 32 | 28 | 2 | PN 10
| 0+040.00 | 9876638.891 | 688038.386 | 1609.969 | 40 | 20 | 1888.125 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 2.565% | 1887.125 | 1 | 0.033158 | 0.062 |  |  |  |  | tank site | 32 | 28 | 2 | PN 10
| 0+060.00 | 9876630.157 | 688029.516 | 1607.735 | 60 | 20 | 1888.089 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -11.17% | 1887.089 | 1 | 0.069158 | 0.098 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+080.00 | 9876624.023 | 688013.015 | 1600.917 | 80 | 20 | 1888.051 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -34.09% | 1887.051 | 1 | 0.10716 | 0.136 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+100.00 | 9876615.426 | 688000.415 | 1595.421 | 100 | 20 | 1888.011 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -27.48% | 1887.011 | 1 | 0.14716 | 0.176 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+120.00 | 9876599.282 | 687984.207 | 1588.142 | 120 | 20 | 1887.959 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -36.39% | 1886.959 | 1 | 0.19916 | 0.228 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+140.00 | 9876598.226 | 687964.56 | 1582.282 | 140 | 20 | 1887.907 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -29.3% | 1886.907 | 1 | 0.25116 | 0.28 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+160.00 | 9876591.762 | 687947.967 | 1577.635 | 160 | 20 | 1887.859 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -23.23% | 1886.859 | 1 | 0.29916 | 0.328 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+180.00 | 9876588.508 | 687946.45 | 1577.047 | 180 | 20 | 1887.811 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -2.94% | 1886.811 | 1 | 0.34716 | 0.376 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+200.00 | 9876583.432 | 687930.105 | 1573.453 | 200 | 20 | 1887.763 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -17.97% | 1886.763 | 1 | 0.39516 | 0.424 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+220.00 | 9876575.52 | 687912.532 | 1569.864 | 220 | 20 | 1887.716 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -17.94% | 1886.716 | 1 | 0.44216 | 0.471 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+240.00 | 9876568.248 | 687895.388 | 1566.916 | 240 | 20 | 1887.672 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -14.74% | 1886.672 | 1 | 0.48616 | 0.515 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+260.00 | 9876567.022 | 687892.575 | 1566.562 | 260 | 20 | 1887.631 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -1.77% | 1886.631 | 1 | 0.52716 | 0.556 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+280.00 | 9876557.853 | 687875.464 | 1564.454 | 280 | 20 | 1887.589 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -10.54% | 1886.589 | 1 | 0.56916 | 0.598 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+300.00 | 9876554.139 | 687876.112 | 1564.141 | 300 | 20 | 1887.547 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -1.565% | 1886.547 | 1 | 0.61116 | 0.64 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+320.00 | 9876545.814 | 687857.797 | 1561.946 | 320 | 20 | 1887.494 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -10.98% | 1886.494 | 1 | 0.66416 | 0.693 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+340.00 | 9876538.423 | 687842.668 | 1560.187 | 340 | 20 | 1887.421 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -8.795% | 1886.421 | 1 | 0.73716 | 0.766 |  |  |  |  | road | 32 | 28 | 2 | PN 10
| 0+360.00 | 9876407.522 | 687934.018 | 1557.67 | 360 | 20 | 1887.354 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -12.58% | 1886.354 | 1 | 0.80416 | 0.833 |  |  |  |  | pipeline route junction to school gate | 32 | 28 | 2 | PN 10
| 0+380.00 | 9876408.657 | 687954.921 | 1558.728 | 380 | 20 | 1887.29 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 5.29% | 1886.29 | 1 | 0.86816 | 0.897 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+400.00 | 9876408.106 | 687975.608 | 1559.313 | 400 | 20 | 1887.196 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 2.925% | 1886.196 | 1 | 0.96216 | 0.991 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+420.00 | 9876410.926 | 687996.721 | 1560.014 | 420 | 20 | 1887.091 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 3.505% | 1886.091 | 1 | 1.0672 | 1.096 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+440.00 | 9876414.702 | 688014.841 | 1560.805 | 440 | 20 | 1886.984 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 3.955% | 1885.984 | 1 | 1.1742 | 1.203 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+460.00 | 9876420.336 | 688035.558 | 1561.811 | 460 | 20 | 1886.875 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 5.03% | 1885.875 | 1 | 1.2832 | 1.312 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+480.00 | 9876426.148 | 688056.351 | 1562.769 | 480 | 20 | 1886.765 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 4.79% | 1885.765 | 1 | 1.3932 | 1.422 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+500.00 | 9876432.175 | 688077.076 | 1563.545 | 500 | 20 | 1886.653 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 3.88% | 1885.653 | 1 | 1.5052 | 1.534 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+520.00 | 9876438.877 | 688097.528 | 1564.357 | 520 | 20 | 1886.519 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 4.06% | 1885.519 | 1 | 1.6392 | 1.668 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+540.00 | 9876446.005 | 688117.51 | 1565.168 | 540 | 20 | 1886.373 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 4.055% | 1885.373 | 1 | 1.7852 | 1.814 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+560.00 | 9876453.779 | 688137.43 | 1565.831 | 560 | 20 | 1886.237 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 3.315% | 1885.237 | 1 | 1.9212 | 1.95 | 0 |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+580.00 | 9876460.926 | 688155.017 | 1566.344 | 580 | 20 | 1886.103 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 2.565% | 1885.103 | 1 | 2.0552 | 2.084 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+600.00 | 9876469.063 | 688173.113 | 1566.849 | 600 | 20 | 1885.965 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 2.525% | 1884.965 | 1 | 2.1932 | 2.222 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10 |  | 22.5
| 0+620.00 | 9876478.748 | 688191.89 | 1567.397 | 620 | 20 | 1885.825 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 2.74% | 1884.825 | 1 | 2.3332 | 2.362 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+640.00 | 9876490.753 | 688208.647 | 1568.164 | 640 | 20 | 1885.692 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 3.835% | 1884.692 | 1 | 2.4662 | 2.495 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+660.00 | 9876504.927 | 688224.933 | 1568.849 | 660 | 20 | 1885.565 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 3.425% | 1884.565 | 1 | 2.5932 | 2.622 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+680.00 | 9876520.618 | 688239.588 | 1569.774 | 680 | 20 | 1885.431 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 4.625% | 1884.431 | 1 | 2.7272 | 2.756 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+700.00 | 9876537.869 | 688253.56 | 1570.753 | 700 | 20 | 1885.285 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 4.895% | 1884.285 | 1 | 2.8732 | 2.902 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+720.00 | 9876555.456 | 688266.539 | 1571.996 | 720 | 20 | 1885.156 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 6.215% | 1884.156 | 1 | 3.0022 | 3.031 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+740.00 | 9876572.838 | 688279.053 | 1573.063 | 740 | 20 | 1885.049 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 5.335% | 1884.049 | 1 | 3.1092 | 3.138 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+760.00 | 9876590.18 | 688291.258 | 1574.203 | 760 | 20 | 1884.949 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 5.7% | 1883.949 | 1 | 3.2092 | 3.238 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+780.00 | 9876607.252 | 688302.787 | 1575.521 | 780 | 20 | 1884.853 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 6.59% | 1883.853 | 1 | 3.3052 | 3.334 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+800.00 | 9876623.501 | 688317.21 | 1577.14 | 800 | 20 | 1884.775 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 8.095% | 1883.775 | 1 | 3.3832 | 3.412 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+820.00 | 9876640.829 | 688327.026 | 1578.286 | 820 | 20 | 1884.701 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 5.73% | 1883.701 | 1 | 3.4572 | 3.486 |  |  |  |  | pipeline route saitoti quarry | 32 | 28 | 2 | PN 10
| 0+840.00 | 9876658.007 | 688335.24 | 1579.194 | 840 | 20 | 1884.599 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 4.54% | 1883.599 | 1 | 3.5592 | 3.588 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+860.00 | 9876677.41 | 688343.778 | 1580.321 | 860 | 20 | 1884.494 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 5.635% | 1883.494 | 1 | 3.6642 | 3.693 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+880.00 | 9876696.977 | 688352.231 | 1581.701 | 880 | 20 | 1884.413 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 6.9% | 1883.413 | 1 | 3.7452 | 3.774 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+900.00 | 9876717.379 | 688358.707 | 1583.099 | 900 | 20 | 1884.329 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 6.99% | 1883.329 | 1 | 3.8292 | 3.858 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+920.00 | 9876736.706 | 688365.152 | 1583.828 | 920 | 20 | 1884.241 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 3.645% | 1883.241 | 1 | 3.9172 | 3.946 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+940.00 | 9876756.516 | 688372.267 | 1584.516 | 940 | 20 | 1884.162 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 3.44% | 1883.162 | 1 | 3.9962 | 4.025 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+960.00 | 9876776.538 | 688378.42 | 1585.4 | 960 | 20 | 1884.055 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 4.42% | 1883.055 | 1 | 4.1032 | 4.132 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 0+980.00 | 9876795.707 | 688389.304 | 1586.076 | 980 | 20 | 1883.987 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 3.38% | 1882.987 | 1 | 4.1712 | 4.2 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 1+000.00 | 9876816.293 | 688395.827 | 1587.176 | 1000 | 20 | 1883.932 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 5.5% | 1882.932 | 1 | 4.2262 | 4.255 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 1+020.00 | 9876836.605 | 688403.389 | 1587.914 | 1020 | 20 | 1883.838 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 3.69% | 1882.838 | 1 | 4.3202 | 4.349 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 1+040.00 | 9876836.668 | 688403.37 | 1587.715 | 1040 | 20 | 1883.741 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -0.995% | 1882.741 | 1 | 4.4172 | 4.446 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 1+060.00 | 9876855.792 | 688412.02 | 1588.635 | 1060 | 20 | 1883.645 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 4.6% | 1882.645 | 1 | 4.5132 | 4.542 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 1+080.00 | 9876874.764 | 688420.553 | 1589.548 | 1080 | 20 | 1883.549 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 4.565% | 1882.549 | 1 | 4.6092 | 4.638 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 1+100.00 | 9876894.609 | 688428.92 | 1590.19 | 1100 | 20 | 1883.461 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 3.21% | 1882.461 | 1 | 4.6972 | 4.726 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 1+120.00 | 9876913.976 | 688436.255 | 1591.114 | 1120 | 20 | 1883.379 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 4.62% | 1882.379 | 1 | 4.7792 | 4.808 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 1+140.00 | 9876933.13 | 688442.847 | 1591.926 | 1140 | 20 | 1883.299 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 4.06% | 1882.299 | 1 | 4.8592 | 4.888 |  |  |  |  | pipeline route corner ya ngombe | 32 | 28 | 2 | PN 10
| 1+160.00 | 9876952.362 | 688452.23 | 1593.232 | 1160 | 20 | 1883.224 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 6.53% | 1882.224 | 1 | 4.9342 | 4.963 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 1+180.00 | 9876970.393 | 688462.374 | 1594.188 | 1180 | 20 | 1883.123 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 4.78% | 1882.123 | 1 | 5.0352 | 5.064 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 1+200.00 | 9876987.888 | 688472.487 | 1595.077 | 1200 | 20 | 1883.004 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 4.445% | 1882.004 | 1 | 5.1542 | 5.183 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 1+220.00 | 9877005.862 | 688484.688 | 1595.788 | 1220 | 20 | 1882.902 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 3.555% | 1881.902 | 1 | 5.2562 | 5.285 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 1+240.00 | 9877022.095 | 688497.675 | 1596.261 | 1240 | 20 | 1882.808 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 2.365% | 1881.808 | 1 | 5.3502 | 5.379 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 1+260.00 | 9877038.176 | 688511.435 | 1596.69 | 1260 | 20 | 1882.695 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 2.145% | 1881.695 | 1 | 5.4632 | 5.492 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 1+280.00 | 9877055.941 | 688524.097 | 1597.713 | 1280 | 20 | 1882.578 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 5.115% | 1881.578 | 1 | 5.5802 | 5.609 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 1+300.00 | 9877074.612 | 688534.842 | 1598.905 | 1300 | 20 | 1882.463 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 5.96% | 1881.463 | 1 | 5.6952 | 5.724 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 1+320.00 | 9877093.311 | 688546.048 | 1600.294 | 1320 | 20 | 1882.349 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 6.945% | 1881.349 | 1 | 5.8092 | 5.838 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 1+340.00 | 9877112.162 | 688556.909 | 1601.706 | 1340 | 20 | 1882.237 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 7.06% | 1881.237 | 1 | 5.9212 | 5.95 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 1+360.00 | 9877132.093 | 688566.501 | 1602.681 | 1360 | 20 | 1882.122 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 4.875% | 1881.122 | 1 | 6.0362 | 6.065 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 1+380.00 | 9877151.83 | 688574.752 | 1603.46 | 1380 | 20 | 1882.002 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 3.895% | 1881.002 | 1 | 6.1562 | 6.185 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 1+400.00 | 9877171.509 | 688582.945 | 1604.335 | 1400 | 20 | 1881.894 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 4.375% | 1880.894 | 1 | 6.2642 | 6.293 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 1+420.00 | 9877191.118 | 688591.63 | 1605.621 | 1420 | 20 | 1881.798 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 6.43% | 1880.798 | 1 | 6.3602 | 6.389 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 1+440.00 | 9877211.272 | 688600.5 | 1607.618 | 1440 | 20 | 1881.681 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 9.985% | 1880.681 | 1 | 6.4772 | 6.506 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 1+460.00 | 9877231.434 | 688610.527 | 1609.38 | 1460 | 20 | 1881.546 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | 8.81% | 1880.546 | 1 | 6.6122 | 6.641 |  |  |  |  | pipeline route | 32 | 28 | 2 | PN 10
| 1+480.00 | 9877244.281 | 688627.954 | 1608.976 | 1480 | 20 | 1881.429 | 0.00046296 | 0.028 | 0.00061544 | 0.75225 | 150 | 0.48904 | 0.028842 | 1887.187 | 1887.187 | 1887.1582 | -2.02% | 1880.429 | 1 | 6.7292 | 6.758 |  |  |  |  | Water Kiosk 3 | 32 | 28 | 2 | PN 10